# Chapter 8 Combined and Special-Purpose FACTS Controllers: UPFC, IPFC, Phase-Angle Regulators, IPC, Current Limiters and Voltage Limiters

## Learning Objectives

After working through this chapter, the reader should be able to:

- derive the active and reactive power delivered by a line equipped with a unified power flow controller (UPFC), construct its circular control region, and compare it with the regions attainable with series compensation or a phase-angle regulator of the same voltage rating;

- explain the real-power exchange between the shunt and series converters of the UPFC, size both converters, model the DC-link energy, and describe the control modes, control structure and the Inez installation;

- analyse the interline power flow controller (IPFC), including the prime-converter constraint, real-power transfer between lines, voltage-margin sharing and the generalized multi-converter controllers;

- derive the behaviour of in-phase voltage regulators, quadrature boosters and ideal phase shifters, and analyse thyristor tap-changers, including their waveforms, harmonics, commutation constraints and ternary winding arrangements;

- derive the power characteristics of the interphase power controller (IPC), its design equations and operating region, and explain the assisted phase-shifting transformer and the decoupling interconnector;

- explain series-resonant, bridge-type and transformer-coupled solid-state fault current limiters, solid-state breakers and transfer switches, and estimate symmetrical and peak fault currents with and without them;

- describe the metal-oxide varistor law and the thyristor-controlled voltage limiter, and calculate clamping levels, inrush transients and absorbed energy;

- formulate research problems on modular converter architectures, coordinated dispatch, impedance-based stability, current-limited operation and protection interaction, and choose a validation method that matches the claim being made.

## 8.1 The Unified Power Flow Controller (UPFC)

### 8.1.1 Concept and circuit

Gyugyi proposed the UPFC in 1991 as a controller that can, within its ratings, act simultaneously or selectively on all the parameters that govern power flow in a line: voltage, impedance and phase angle [1], [2], [3]. Figure 8.1 shows its circuit. Two voltage-source converters (VSCs) share a DC capacitor. Converter 2 is connected in series with the line through an insertion transformer and injects a voltage Vpq of controllable magnitude 0≤Vpq≤Vpq,max and controllable angle 0≤ρ<2π. Converter 1 is connected in shunt through a coupling transformer. Its first task is to supply or absorb, through the DC link, the real power that converter 2 exchanges with the line. It can also generate or absorb reactive power independently, exactly as a STATCOM does, to regulate the bus voltage.

Figure 8.1. UPFC circuit: shunt and series voltage-source converters sharing a DC link.

The UPFC is best understood as an energy-coupled combination of the shunt VSC of Chapter 6 and the series VSC of Chapter 7. If the two converters were electrically independent, the series converter could exchange with the line only the real power available from its own DC source, which in practice means none in steady state. Connecting the DC terminals changes this. The shunt converter draws real power from the AC bus, passes it through the DC link, and allows the series converter to inject a voltage at any angle with respect to the line current. This is the physical origin of the two-dimensional P-Q control capability.

The important point is what passes through the DC link and what does not. The commanded series voltage can be resolved into a component in phase with the line current and a component in quadrature with it. The quadrature component exchanges reactive power that is generated or absorbed inside converter 2, as in an SSSC. The in-phase component exchanges real power, and only this average real power, together with converter losses and the small change in capacitor energy during transients, travels through the DC link to converter 1 and from there back to the AC system (Figure 8.2). Seen from the line, the UPFC is therefore an ideal series voltage source of any phase angle. It can emulate a capacitive or inductive series reactance, an in-phase voltage regulator, a phase shifter, or any combination, and it can move between these functions within a few cycles.

Figure 8.2. Energy and control paths in a UPFC. Only the real-power imbalance is exchanged through the common DC link; reactive power is handled locally at each converter.

The shunt converter therefore has two simultaneous duties. The first is energetic: it regulates the DC-link voltage by supplying the real power demanded by the series converter plus the losses. The second is local AC support: within its current rating it injects or absorbs reactive current to regulate the sending-bus voltage. Both duties share one current limit, so they cannot be treated as independent, unlimited services.

### 8.1.2 Power-flow equations

Consider the two-machine system with the UPFC at the sending end of a lossless line of reactance X. Take the receiving voltage as the reference, Vr=Vr∠0, the sending voltage as Vs=Vs∠δ, and write the series injection as Vpq=Vpq∠(δ+ρ), so that ρ is measured from the sending-end voltage. Kirchhoff’s voltage law around the line gives

|  | I=Vs+Vpq−VrjX | (8.1) |
| --- | --- | --- |

where I is the line current phasor. The complex power delivered to the receiving end, Sr=VrI*, separates into

|  | Pr=VsVrXsinδ+VrVpqXsin(δ+ρ), Qr=VsVrcosδ−Vr2X+VrVpqXcos(δ+ρ) | (8.2) |
| --- | --- | --- |

where Pr and Qr are the active and reactive power delivered to the receiving bus. For Vs=Vr=V the uncompensated values are P0=(V2/X)sinδ and Q0=−(V2/X)(1−cosδ), and Equation (8.2) can be written as

|  | (Pr−P0)2+(Qr−Q0)2=VVpqX2 | (8.3) |
| --- | --- | --- |

As ρ sweeps a full turn at fixed Vpq, the operating point traces a circle centred on the uncompensated point (P0,Q0) with radius VVpq/X. Allowing any magnitude up to Vpq,max fills the disk. The centre slides along the uncompensated locus as δ changes, but the radius does not depend on δ (Figure 8.3). Even at δ=0, where an uncompensated line carries nothing, the UPFC can drive up to VVpq,max/X of active power in either direction.

Figure 8.3. UPFC control regions in the Pr-Qr plane at δ=0∘, 30∘, 60∘ and 90∘ (V=1 pu, X=0.5 pu, Vpq,max=0.25 pu).

The attainable active power at any angle therefore lies in the band P0±VVpq,max/X (Figure 8.4). Maximum power at a given angle is obtained with sin(δ+ρ)=1, that is, with Vpq leading the receiving voltage by 90∘; at that point the reactive power is unchanged from Q0. Figure 8.5 shows how both receiving-end powers vary as the injection angle rotates. The active and reactive responses are in quadrature, which is the reason a single-angle device cannot set both of them independently.

Figure 8.4. Range of transmittable active power with a UPFC versus transmission angle (V=1 pu, Vpq,max=0.25 pu, X=0.5 pu).

Figure 8.5. Receiving-end active and reactive power versus injection angle for V=1 pu, X=0.5 pu, δ=30∘ and Vpq=0.25 pu. The two curves are the projections of the control circle of Equation (8.3).

The disk is a kinematic result for an ideal, lossless network. A real UPFC occupies only the part of it that also satisfies the series-voltage limit, the line-current limit, the series- and shunt-converter MVA limits, the DC-link voltage band and the semiconductor thermal limits. These constraints are introduced in Sections 8.1.4 and 8.1.6.

#### Example 8.1. UPFC control circle

For V=1.0 pu, X=0.5 pu, δ=30∘ and Vpq,max=0.25 pu, find the uncompensated operating point, the radius of the ideal control circle and the attainable range of Pr.

Solution. P0=(V2/X)sinδ=2sin30∘=1.00 pu and Q0=−2(1−cos30∘)=−0.268 pu. The radius is R=VVpq,max/X=0.25/0.5=0.50 pu. The extreme active powers lie at the horizontal ends of the disk, so Pr,max=1.50 pu and Pr,min=0.50 pu. Every point of the disk is geometrically reachable, but converter current, series-transformer voltage and shunt-converter real-power capability must still be checked before a point is accepted as feasible.

### 8.1.3 Comparison with single-parameter controllers

Figure 8.6 compares, at δ=30∘, the operating points that three controllers with the same injected-voltage limit can reach. A controllable series reactance (TCSC or SSSC) injects voltage in quadrature with the current, so it can only move the operating point along a curve through (P0,Q0). A phase-angle regulator injects voltage in quadrature with the bus voltage and moves the point along a different curve. Only the UPFC, free to choose the angle of injection, fills the whole disk. It can therefore set active and reactive flow independently, which no single-parameter device can do [4], [5].

Figure 8.6. Attainable Pr-Qr at δ=30∘: UPFC, controllable series compensation and phase-angle regulator with the same injected-voltage limit.

The same hardware reproduces these familiar controllers simply by constraining the direction of Vpq (Figure 8.7). For voltage regulation the injection is aligned with Vs. For series-reactance emulation it is tied to the line current and kept in quadrature with it, leading the current (in the boosting sense) for capacitive compensation. For phase-angle regulation it is chosen so that the line-side voltage Vs′ rotates by a commanded angle with unchanged magnitude. Automatic power-flow control removes all directional restrictions and computes whatever phasor drives the measured P and Q to their references.

Figure 8.7. Phasor interpretation of four UPFC series-injection modes. Vs′=Vs+Vpq is the line-side voltage and I the line current.

### 8.1.4 Internal power exchange and ratings

The complex power supplied by the series converter to the line is

|  | Sse=Pse+jQse=VpqI* | (8.4) |
| --- | --- | --- |

where Pse and Qse are the real and reactive power delivered by the series converter. In a lossless UPFC in steady state the DC link must balance:

|  | Psh+Pse=0 | (8.5) |
| --- | --- | --- |

where Psh is the real power delivered by the shunt converter to the AC system. The shunt converter therefore draws Pse from the bus (or returns it) in addition to its own reactive output Qsh, and its rating must satisfy

|  | Ssh=Pse2+Qsh2≤VbusIsh,max, Sse=VpqI≤Vpq,maxImax | (8.6) |
| --- | --- | --- |

Figure 8.8 plots Pr, Pse and Qse against ρ for a representative case. The real power circulated through the link is small compared with the change in line power it produces (0.067 pu of link power for a 0.5 pu increase in line power in Example 8.25), while the series converter’s reactive power is considerably larger. The series converter rating is set by Vpq,maxImax. The shunt converter is often rated similarly, so that it can operate as a full STATCOM when the series converter is out of service.

Figure 8.8. Receiving-end power and series-converter real and reactive power versus injection angle (δ=30∘, Vpq=0.25 pu, X=0.5 pu).

#### Example 8.2. Series-converter real-power requirement

A UPFC series converter injects 0.12 pu at an angle of 30∘ with respect to a 0.90 pu line current. Find the converter real and reactive power on the same three-phase base.

Solution. With the current as reference, Sse=VpqI*=0.12×0.90∠30∘=0.108∠30∘ pu. Hence Pse=0.108cos30∘=0.0935 pu and Qse=0.108sin30∘=0.0540 pu. The shunt converter must supply about 0.0935 pu of real power through the DC link, plus losses. The 0.054 pu of reactive power is produced inside the series converter and does not cross the link.

#### Example 8.3. Shunt-converter current allocation

A shunt VSC connected to a 1.0 pu bus must draw 0.18 pu of real power to support the UPFC DC link and inject 0.24 pu of reactive power for voltage support. Determine its apparent-power duty and current.

Solution. Ssh=0.182+0.242=0.30 pu. At V=1.0 pu the current magnitude is also 0.30 pu. Once the converter reaches its current limit, real-power balancing and reactive support compete for the same current and cannot be allocated independently.

### 8.1.5 Operating and control modes

The shunt converter operates in one of two modes. In VAR control it follows a reactive power (or reactive current) reference. In automatic voltage control, the usual mode, it adjusts reactive current to regulate the bus voltage at the point of connection along a droop characteristic. In either mode a DC-voltage regulator adds the active-current component that balances the series-converter real power and the losses.

The series converter offers five functional modes. They are control objectives, not different power circuits:

- Direct voltage injection. The converter injects the commanded Vpq and ρ directly. Special cases are an injection in quadrature with the current (SSSC-like reactive compensation) and an injection in phase with the bus voltage (voltage regulation).

- Bus voltage regulation. The injection is kept in phase with the sending-end voltage and its magnitude regulates the voltage at the line-side terminal.

- Line impedance compensation. The injection is made proportional to the line current with a chosen phase, emulating a series reactance and, if desired, a series resistance.

- Phase-angle regulation. The injection is chosen so that the line-side voltage is shifted by a commanded angle without change of magnitude.

- Automatic power-flow control. The most general mode, in which closed outer loops around the measured line P and Q compute the series voltage, so that the commanded flows are maintained in spite of network changes.

### 8.1.6 Dynamic model, control structure and limits

For dynamic studies the DC capacitor cannot be treated as an algebraic power-transfer path. Its stored energy is Wdc=12CdcVdc2. With positive Psh and Pse denoting real power delivered from the converters to the AC system, the energy balance is

|  | dWdcdt=ddt12CdcVdc2=−Psh+Pse+Ploss | (8.7) |
| --- | --- | --- |

and for small deviations about the operating voltage Vdc0,

|  | CdcVdc0d ΔVdcdt≈−ΔPsh+ΔPse | (8.8) |
| --- | --- | --- |

Equation (8.5) is therefore valid only after the energy transient has settled. A temporary mismatch moves Vdc, and the shunt-converter DC-voltage loop supplies the active current that restores it.

#### Example 8.4. DC-link energy deviation

A 20 mF UPFC DC capacitor operates at 20 kV. For 15 ms the series converter draws 6 MW more real power from the link than the shunt converter supplies. Neglect losses and find the DC voltage after the event.

Solution. Initial energy W1=12CV12=0.5×0.020×(20 000)2=4.00 MJ. The deficit is 6×106×0.015=0.09 MJ, so W2=3.91 MJ and V2=2W2/C=19.77 kV, a 1.1 % dip. The linearized Equation (8.8) gives ΔVdc≈−0.09×106/(0.020×20 000)=−225 V, which agrees closely.

Figure 8.9 shows a typical vector-control structure. A phase-locked loop provides the reference angle for both converters. For the series converter, Pref and Qref are converted into d- and q-axis line-current references, and a current controller with decoupling computes the series voltage, limited to Vpq,max. For the shunt converter, a DC-voltage regulator produces the active-current reference that keeps the link charged, and an AC-voltage (or VAR) regulator produces the reactive-current reference. Supplementary loops add power-oscillation damping and transient-stability functions to the series reference.

Figure 8.9. UPFC control structure: series converter in automatic power-flow control, shunt converter regulating DC and AC voltage.

The inner current or voltage loops must be appreciably faster than the outer power, AC-voltage and DC-voltage loops. Bandwidth separation reduces interaction, but it does not remove the coupling that exists through the network and the DC link. Anti-windup is required wherever a reference saturates.

The ideal control disk is not a converter capability curve. At every requested operating point the controller must check series-voltage magnitude, line current, series-converter MVA, shunt-converter current, transformer MVA, DC-link voltage and semiconductor temperature. In normal operation the outer P-Q loop may have full authority. During a severe voltage depression or fault, current limiting overrides it, because semiconductor survival has priority over tracking a power-flow reference. A common priority order is converter protection and DC-link energy first, then the remaining current margin for reactive support. The exact order is manufacturer and application dependent and should be represented explicitly in EMT studies.

A UPFC is not energized by simply enabling both PWM bridges. A typical sequence precharges the DC link, verifies transformer and bus conditions, synchronizes the converter reference frame, enables the shunt converter to establish Vdc, and only then releases the series converter from bypass. Shutdown reverses the sequence. During an internal converter fault or a severe external fault, the series converter is blocked and a thyristor bypass across the insertion-transformer secondary carries the line current, so the transmission line stays in service even though the power-flow controller is unavailable.

Figure 8.10 shows the qualitative response to a step in the automatic power-flow references. P and Q move to their new values with a controlled transient while Vdc is disturbed only temporarily. A sustained drift of Vdc indicates a real-power imbalance or shunt-converter saturation. Large oscillations in P or Q point to inadequate damping, loop interaction, measurement delay or an operating point near a limit.

Figure 8.10. Illustrative UPFC response to a power-flow reference change (normalized). The curves show the expected relationship among P, Q and DC-link voltage, not a universal tuning.

Two dynamic duties deserve separate mention. During electromechanical oscillations, the supplementary controller modulates the series-voltage command so that the resulting electrical-power component opposes the speed or angle deviation. During a line fault, the objective changes at once from power-flow tracking to converter protection: series injection is limited, blocked or bypassed according to current and voltage stress, and normal control is restored only after the post-fault network is judged stable. A simulation that keeps enforcing Pref and Qref through a severe fault produces unrealistically large converter commands and overstates the transient-stability benefit.

### 8.1.7 UPFC with a fixed phase shifter

A UPFC can be combined with a fixed, mechanically tapped phase-shifting transformer. The fixed shifter moves the centre of the control circle to the point that corresponds to the shifted angle, and the UPFC provides fast control around that new centre. The motivation is rating reduction. If the steady requirement is Vfix and the dynamic correction is ΔV, the converter need only be rated for the envelope of ΔV rather than for Vfix+ΔV. The price is flexibility, because the fixed component cannot be removed electronically during an emergency.

#### Example 8.5. Fixed phase shifter plus UPFC

A corridor requires a steady 12∘ phase shift but only ±4∘ of fast modulation for damping and dispatch. If an ideal fixed phase shifter supplies 12∘, what range must the UPFC series converter provide, and what is the approximate rating saving on a 1 pu voltage base?

Solution. The converter needs to cover only −4∘ to +4∘ about the fixed point, giving a total controllable shift of 8∘ to 16∘. From ​Vσ​=2Vsin(σ/2), a 16∘ shift needs 0.278 pu of injection whereas 4∘ needs 0.070 pu, so the series-converter voltage rating falls to roughly one quarter.

### 8.1.8 Field experience: the Inez UPFC

The first UPFC was installed at the Inez substation of American Electric Power in eastern Kentucky and entered test operation in May 1998 [6], [7]. It was a joint project of AEP, EPRI and Westinghouse (later Siemens). It consists of two identical ±160 MVA GTO-thyristor voltage-sourced converters with harmonic-neutralizing multi-pulse transformer arrangements, which can be configured as a STATCOM, an SSSC or a UPFC. Its purpose was to support the voltage of a heavily loaded 138 kV area and to control power flow on a new high-capacity line. Inez established the practicality of converter-based power-flow control, and the same converter building blocks were later used in the NYPA convertible static compensator at Marcy (Section 8.2.4). Present installations use modular multilevel converters instead (Section 8.8.1), but the energy-balance and series-injection principles are unchanged.

## 8.2 The Interline Power Flow Controller (IPFC)

### 8.2.1 Concept

Gyugyi, Sen and Schauder proposed the IPFC to compensate several lines leaving one substation [8]. Each line is given its own series converter, and all converters share a common DC link (Figure 8.11). Each converter can provide reactive series compensation to its own line, as an SSSC would. In addition, because the converters share the DC link, any converter can deliver real power to its line provided another converter draws the same real power from its own line. The IPFC can therefore transfer real power between lines: it can relieve an overloaded line by shifting active power to an underloaded one, equalize both active and reactive flows, and compensate resistive as well as reactive voltage drops.

Figure 8.11. Two-converter IPFC with series converters in two lines and a common DC link.

The common DC link creates no energy. In an IPFC without a shunt converter or storage, the algebraic sum of the average real powers exchanged by all series converters must be zero apart from losses and transient changes of capacitor energy. For N series converters (Figure 8.12)

|  | k=1NPk,pq+dWdcdt+Ploss=0 | (8.9) |
| --- | --- | --- |

with signs defined at the converter AC terminals. This single constraint distinguishes an IPFC from several independent SSSCs and explains why the individual line commands are coupled.

Figure 8.12. Generalized IPFC with several series converters sharing one DC link at a common substation.

### 8.2.2 Constrained operation of the prime converter

In a two-converter IPFC, converter 1 (the prime converter) is chosen to control line 1 fully, with its injected voltage V1pq free in magnitude and angle. Its line then follows Equation (8.2) and Equation (8.3) exactly as with a UPFC. The difference lies in where the real power comes from. The series power supplied by converter 1 to line 1 must be absorbed by converter 2:

|  | P1pq=ReV1pqI1*, P1pq+P2pq=0 | (8.10) |
| --- | --- | --- |

where P1pq and P2pq are the real powers delivered to lines 1 and 2 by their converters and I1 is the current of line 1. Converter 2 must therefore inject into line 2 a voltage whose component in phase with I2 absorbs exactly P1pq. That fixes one degree of freedom of converter 2. The other, its quadrature component, remains free for reactive compensation of line 2, but only within the voltage margin left inside its circular limit (Figure 8.13):

|  | V2p=−P1pqI2, ​V2q​≤V2,max2−V2p2 | (8.11) |
| --- | --- | --- |

Figure 8.13. Voltage decomposition of (a) the prime converter and (b) the supporting converter, each referred to its own line current. Real-power support consumes part of the supporting converter’s voltage capability.

The operating region of line 1 is a full disk only if line 2 can supply the required real power within its converter rating. Otherwise line 1’s region is clipped to the band ​P1pq​≤V2,maxI2 (Figure 8.14). Example 8.32 works through a typical case: at δ=30∘, X=0.5 pu and Vpq,max=0.25 pu, holding Q1r=0 while raising P1r to 1.42 pu requires converter 1 to supply 0.19 pu of real power. Converter 2, with the same voltage rating, can absorb it in two ways, one of which also raises the power in line 2 to 1.23 pu.

Figure 8.14. Prime-line operating region of an IPFC at δ=30∘ (V=1 pu, X=0.5 pu, V1pq,max=0.25 pu). Only the shaded band is reachable when the supporting converter can exchange at most 0.10 pu or 0.05 pu of real power.

In a multi-line installation the prime role need not be permanently assigned. A supervisory controller can redistribute real-power duty according to line loading, converter temperature and remaining voltage margin (Figure 8.15).

Figure 8.15. Illustrative redistribution of active power among three lines by coordinated IPFC control. The total transfer is unchanged; the overloaded corridor is relieved.

#### Example 8.6. Real-power redistribution in a three-converter IPFC

Three series converters share a common DC link. Converter 1 delivers 0.18 pu of real power to line 1 and converter 2 absorbs 0.07 pu from line 2. Neglecting losses and DC-energy change, find the real power of converter 3.

Solution. From Equation (8.9), P1+P2+P3=0. Taking delivery to a line as positive, P3=−(0.18−0.07)=−0.11 pu: converter 3 must absorb 0.11 pu from line 3. An IPFC can redistribute real power, but it cannot supply net real power to all lines at once unless a shunt converter, storage or another real-power port is added.

#### Example 8.7. Remaining quadrature margin of a supporting converter

A supporting converter is limited to V2,max=0.20 pu and carries I2=1.0 pu. It must absorb 0.12 pu of real power for the prime line. Find the largest quadrature component it can still inject, and repeat for a line current of 1.5 pu.

Solution. At I2=1.0 pu, V2p=−0.12 pu and ​V2q​≤0.202−0.122=0.16 pu. At I2=1.5 pu the same power needs only V2p=−0.08 pu, leaving 0.04−0.0064=0.183 pu. A heavily loaded supporting line is therefore the better donor, because it can exchange the same real power with a smaller in-phase voltage.

### 8.2.3 Generalized and multi-converter controllers

The UPFC and the IPFC are special cases of a family built from voltage-source converters on a common DC bus. A generalized UPFC (GUPFC) adds a shunt converter to an IPFC: the shunt converter regulates the bus voltage and supplies the net real-power imbalance of the series converters, so that each line can be controlled fully. A generalized IPFC with n series converters satisfies the single steady-state constraint

|  | k=1nPk,pq=Psh+Pstorage−Ploss | (8.12) |
| --- | --- | --- |

where Pk,pq is the real power delivered by the kth series converter, Psh that drawn by any shunt converter from its bus, Pstorage that drawn from any energy store and Ploss the converter losses. Each converter adds two degrees of freedom and the DC balance removes one. Converter count alone does not define capability; the connection topology and the DC-link energy paths do [9], [10].

#### Example 8.8. IPFC DC-link voltage drift

A 10 mF DC capacitor operates at 15 kV. For 20 ms the algebraic converter-power imbalance removes 3 MW from the capacitor. Neglect losses and find the final DC voltage.

Solution. Initial energy 0.5×0.010×15 0002=1.125 MJ. The energy removed is 3×106×0.020=0.060 MJ, leaving 1.065 MJ, so Vdc2=2×1.065×106/0.010=14.59 kV. Even a short mismatch produces a visible DC excursion, which is why dynamic IPFC models must not replace the capacitor by a constant-voltage source.

### 8.2.4 The convertible static compensator

The New York Power Authority’s convertible static compensator (CSC) at the Marcy 345 kV substation made this flexibility practical [11]. Two 100 MVA converters, a shunt transformer and two series transformers in different lines can be configured by switching as one or two STATCOMs, one or two SSSCs, a UPFC or an IPFC. The STATCOM stage was placed in commercial operation in April 2001 and the full CSC was completed in July 2004. Functional convertibility means that a single investment provides a STATCOM today and a power-flow controller tomorrow, as system needs change.

## 8.3 Voltage and Phase-Angle Regulators (TCVR and TCPAR)

### 8.3.1 Principle

A voltage regulator adds an in-phase voltage ΔV to the bus voltage, changing its magnitude. A phase-angle regulator (PAR) adds a voltage that shifts its phase. Figure 8.16 shows the three common forms. The in-phase regulator changes only magnitude. The quadrature booster adds a voltage Vσ at 90∘, which shifts the phase by σ=tan−1(Vσ/Vs) but also raises the magnitude to Vs2+Vσ2. The ideal phase shifter adds a voltage at an angle (π+σ)/2 to Vs, so that the magnitude is unchanged and the phase shifts by σ, with

|  | ​Vσ​=2Vssinσ2 | (8.13) |
| --- | --- | --- |

Geometrically, the injection is the chord between two equal-radius phasors separated by σ.

Figure 8.16. Phasor diagrams of (a) an in-phase voltage regulator, (b) a quadrature booster and (c) an ideal phase shifter (σ=20∘).

With an ideal phase shifter at the sending end of a lossless line, the transmitted power becomes

|  | P=V2Xsin(δ±σ) | (8.14) |
| --- | --- | --- |

where σ is the phase shift and the sign depends on the boost convention. The power-angle curve is shifted sideways rather than scaled (Figure 8.17). A phase shifter therefore does not raise the maximum transmissible power of a single line. It lets the operator choose the power at a given network angle, which is exactly what is needed to control loop flows in meshed networks, to keep a heavily loaded line within its limit, or to pick up power on an underused path. In transients, rapidly increasing σ after a fault keeps the electrical power high while the machine accelerates, which enlarges the decelerating area, and modulating σ with speed deviation adds damping.

Figure 8.17. Power-angle curves with a phase-angle regulator: the curve shifts sideways by σ without change of peak.

A quadrature booster on a lossless line delivers P=(Vs,effVr/X)sin(δ+σ) with Vs,eff=Vs2+Vσ2, so it slightly raises the reactive power flow as well. For small Vσ/Vs the magnitude error is second order, which is why the approximation is acceptable at modest angles, but the difference matters for rating and reactive-power calculations. In meshed networks with X≫R, an in-phase regulator mainly controls reactive loop flow and a quadrature regulator mainly controls active loop flow.

#### Example 8.9. Quadrature-booster magnitude error

A 1.0 pu bus receives a quadrature injection of 0.20 pu. Find the resulting voltage magnitude and phase shift, and the injection an ideal phase shifter needs for the same angle.

Solution. ​V′​=1+0.22=1.0198 pu and σ=tan−10.2=11.31∘. The shift is accompanied by a 1.98 % magnitude rise. An ideal phase shifter needs 2sin(5.655∘)=0.197 pu at an angle of 95.7∘ to Vs and leaves the magnitude at 1.0 pu.

### 8.3.2 Thyristor tap-changers

The classical PAR or voltage regulator is a transformer with a mechanical on-load tap changer, which is slow and wears with every operation. Replacing the mechanical changer by thyristor switches makes the device fast enough for dynamic control. In its simplest form, two taps V1 and V2 of a winding are each connected to the output through an antiparallel thyristor pair. With a resistive load, firing the upper-tap switch at a delay α in each half cycle produces the output waveform of Figure 8.18. The output follows v1 up to α and v2 afterwards, so its fundamental varies continuously between V1 and V2. Because the waveform jumps at α, the output contains odd harmonics whose amplitude depends on V2−V1 and α.

Figure 8.18. Thyristor tap-changer with a resistive load: output voltage for V1=0.9 pu, V2=1.1 pu and α=60∘ (left), and fundamental, 3rd and 5th harmonics versus α (right).

Commutation deserves explicit attention. With an inductive load the current continues after the voltage zero, and with a capacitive load it leads the voltage, so the commutation instants move. The tap-changing circuit must never connect two unequal taps together through conducting valves, because the resulting circulating current is limited only by the leakage impedance of the tap section. Safe transfer therefore requires that the outgoing thyristor has stopped conducting before the incoming one fires, which is why practical gate logic uses current polarity and tap-voltage polarity rather than voltage phase alone, together with interlocks and timed transfer states.

To avoid harmonics altogether, the tap-changer can be operated in discrete steps by switching whole cycles; a transient then occurs only when the tap changes. With identical windings the number of levels grows only linearly with the number of switches. With windings proportioned in a ternary ratio 1:3:9:…, each connected through a bridge that can add it with positive or negative polarity or bypass it, L windings give 3L levels (Figure 8.19):

|  | Nlevels=3L, ΔVmax=3L−12Vstep | (8.15) |
| --- | --- | --- |

where L is the number of winding sections, Vstep the voltage of the smallest section and ΔVmax the largest injected voltage in each direction. Applied to an in-phase winding, this gives a thyristor-controlled voltage regulator (TCVR); applied to a quadrature winding excited from the other two phases, a thyristor-controlled phase-angle regulator (TCPAR).

Figure 8.19. Injected-voltage levels of a ternary-proportioned three-winding regulator.

#### Example 8.10. Ternary regulator

A three-section ternary regulator has Vstep=4 kV. Find the section voltages, the number of levels and the maximum positive injection.

Solution. The sections are 4, 12 and 36 kV. The number of levels is 33=27, and the maximum positive injection is 4×(27−1)/2=52 kV. Ternary proportioning obtains many levels with few sections, but insulation, transformer complexity and valve coordination still govern the practical design.

### 8.3.3 Converter-based regulators

A voltage-source converter connected in series through a transformer can inject a voltage of any phase. If it is used as a voltage regulator or phase-angle regulator, it must exchange real power with the line, because the injected voltage is not in quadrature with the current. That real power has to come from a shunt converter or an energy store: a converter-based PAR is, in effect, a UPFC operated in phase-angle regulation mode. Hybrid schemes combine a mechanically tapped phase shifter for the bulk angle with a small converter for fast trimming and damping. A transformer-only alternative is the Sen transformer, which synthesizes a series voltage of selectable magnitude and angle from tapped windings of a shunt-connected unit [12]; it gives UPFC-like steady-state control at transformer cost but with tap-changer speed.

## 8.4 The Interphase Power Controller (IPC)

### 8.4.1 Motivation and concept

Interconnecting two strong networks raises short-circuit levels, often beyond the ratings of existing breakers. The conventional remedies are to leave bus-tie breakers open, to operate subtransmission radially or to split substation buses, all of which sacrifice flexibility and sometimes reliability. The interphase power controller, developed in Canada in the 1990s [13], offers a passive alternative. Each phase of the tie consists of two parallel branches, one inductive and one capacitive, connected to voltages that are phase-shifted by angles ψ1 and ψ2 (Figure 8.20). The phase shifts are obtained either from phase-shifting transformers or by connecting the branches to other phases of the sending network, hence the name. The basic IPC uses only reactors, capacitors and transformers: it generates no harmonics, has no switching losses and needs little maintenance. Power electronics can be added where fast control is needed.

Figure 8.20. IPC equivalent circuit: inductive and capacitive branches fed from phase-shifted voltages.

### 8.4.2 Power characteristics

Let the branch susceptances be B1 (inductive, B1=−1/XL<0) and B2 (capacitive, B2=+1/XC>0). Branch k sees an angle δBk=δSR−ψk, where δSR=δS−δR. Summing the two branch flows gives

|  | P=−VSVRB1sinδB1+B2sinδB2 | (8.16) |
| --- | --- | --- |

|  | −QS=k=1,2​VS2−VSVRcosδBkBk, QR=k=1,2​VR2−VSVRcosδBkBk | (8.17) |
| --- | --- | --- |

where P is the transmitted active power and QS and QR are the reactive powers at the sending and receiving ends. Subtracting the two reactive equations gives −QS=(B1+B2)(VS2−VR2)+QR, so that with B1=−B2 the reactive powers at the two ends are equal and opposite whatever the voltages.

In the IPC120 the branches of each phase are connected, through a Y-y6 transformer, to the inverted voltages of the two other phases, which lie at ψ1=−60∘ and ψ2=+60∘ from the phase voltage; the two connection points are thus 120∘ apart. With ​B1​=​B2​=1/X and VS′=VS/n for transformer ratio n, Equation (8.16) and Equation (8.17) combine into

|  | P&=PmaxcosδSR−ψ1+ψ22sinψ2−ψ12QR&=−PmaxsinδSR−ψ1+ψ22sinψ2−ψ12 | (8.18) |
| --- | --- | --- |

with Pmax=2VS′VR/X. For the symmetric IPC120 this is P=0.866PmaxcosδSR. The power is a cosine of the angle and is flat near δSR=0: over ±25∘ it changes by less than 10 % (Figure 8.21). An ordinary tie line, whose power is a sine of the angle, would swing from strong forward to strong reverse flow over the same range. The IPC also delivers non-zero power at zero angle, because its branches see the phase-shifted voltages.

Figure 8.21. Active and receiving-end reactive power of an IPC120 versus angle, compared with an ordinary tie.

The flat characteristic is not produced by feedback control. It results from superposing the powers of an inductive branch and a capacitive branch whose applied voltages are displaced in phase (Figure 8.22). As the external angle increases, the inductive-branch power sin(δSR+60∘) rises while the capacitive-branch power sin(60∘−δSR) falls, and around the design point their first-order changes cancel. The reactive powers do not cancel in the same way, so branch reactive circulation can be substantial even when the net active power is well behaved. Component ratings must be based on branch current and voltage, not on the net MW transfer alone.

Figure 8.22. Exact decomposition of IPC120 active power into inductive- and capacitive-branch contributions (VS=VR=1 pu, ​Bk​=1 pu). Their opposing slopes produce the flat total 3cosδSR.

#### Example 8.11. IPC branch-current rating

An IPC transfers 300 MW at unity net power factor on a 230 kV three-phase link, but internal branch currents are 1.35 times the line current because of reactive circulation. Estimate the line current and the branch-current rating.

Solution. I=300×106/(3×230×103)=753 A. Each branch should be rated for at least 1.35×753=1017 A before overload margin is added. The net terminal power factor reveals nothing about this internal circulation; branch equipment must be rated from the branch phasors.

### 8.4.3 Design equations, fault behaviour and variants

For a specified P and QR at a given angle, Equation (8.16) and Equation (8.17) are linear in B1 and B2 and can be solved directly. For the IPC120 the solution is

|  | B1=P2VR−VScosδSR−3VSsinδSR−QRVS3cosδSR−sinδSR3VSVRVS−2VRcosδSR | (8.19) |
| --- | --- | --- |

|  | B2=−P2VR−VScosδSR+3VSsinδSR−QRVS3cosδSR+sinδSR3VSVRVS−2VRcosδSR | (8.20) |
| --- | --- | --- |

where B1 and B2 are the required branch susceptances. Substituting the results of Example 8.43 (P=1.673 pu, QR=−0.448 pu at δSR=15∘) returns B1=−1.00 pu and B2=+1.00 pu, which is a useful check. The IPC limits its own fault contribution because a fault at one terminal leaves the other terminal feeding through one branch impedance, never through the parallel combination.

The IPC family should be separated into variants because their objectives differ [13], [14]. The IPC120 uses ±60∘ internal shifts and matched susceptances to obtain the flattest characteristic. An injection IPC uses smaller shifts produced by series injection transformers, reducing transformer voltage rating. The decoupling interconnector (DI) tunes the two branches to parallel resonance at system frequency; its terminal voltages are then decoupled, and it contributes almost nothing to faults on either side, which allows ties that would otherwise be impossible because of short-circuit levels. The fault-current-limiting transformer (FCLT) is a DI simplified for use in parallel with conventional transformers, raising a station’s capacity without raising its short-circuit level. For transmission, where complete decoupling would harm stability, the parallel circuit is detuned. The simplest version is the assisted phase-shifting transformer (APST): an existing PST with a reactive impedance in parallel. The first APST entered service in June 1998 at Plattsburgh, New York, on the tie to Vermont, where inductors were added in parallel with an existing phase-angle regulator to raise its transfer capacity.

### 8.4.4 Operating region and retrofitting of PSTs

Seen from the network, a PST with leakage reactance XT transfers P≈(δSR−ψ)/XT for small angles. Its operating region in the P-δSR plane is a band of slope 1/XT bounded by the tap limits ψmin and ψmax and by winding-current limits. Adding a parallel branch of reactance Xp adds δSR/Xp to the power. With an inductor (Xp>0) the band becomes steeper and the capacity rises; with a capacitor (Xp<0) the slope falls, and with Xp=−XT the characteristic becomes flat, which is the IPC behaviour. Figure 8.23 compares the two operating regions.

Figure 8.23. Operating regions of a PST alone and of the same PST with a parallel capacitor (IPC), small-angle approximation.

## 8.5 Solid-State Current Limiters, Breakers and Transfer Switches

### 8.5.1 Fault current limitation

Growing generation and interconnection raise fault levels above the interrupting ratings of existing breakers. Fault-current-limiting devices fall into two broad classes (Figure 8.24) [15]. Single-shot devices, such as current-limiting fuses and pyrotechnic limiters, must be replaced after each operation. Multi-operation devices include solid-state, hybrid, saturable-core and superconducting limiters. A solid-state current limiter (SSCL) inserts an impedance into the faulted circuit within a few milliseconds, before the first current peak, so that the downstream breaker sees a reduced current.

Figure 8.24. Classification of fault-current-limiting technologies. This chapter concentrates on solid-state and hybrid implementations and retains superconducting limiters for comparison.

A good limiter presents very small impedance and loss in normal operation, responds before the prospective current reaches its first peak, inserts enough impedance during the fault, coordinates with relays and breakers, withstands the associated energy and recovery voltage, and returns to service quickly after clearance. These requirements conflict. A large limiting impedance improves current reduction but raises recovery voltage and stored energy; a semiconductor path improves speed but adds conduction loss and thermal stress.

For preliminary design the symmetrical fault current follows from the Thevenin equivalent, If=Vph/​Zth+Zlim​. For a predominantly inductive source the required limiting reactance is

|  | Xlim=VphIf,lim−Xs | (8.21) |
| --- | --- | --- |

where Xlim is the reactance the limiter must insert, Vph the phase voltage, If,lim the permitted symmetrical RMS fault current and Xs the source reactance. This is only an RMS screen. The first asymmetrical peak depends on the fault inception angle and the X/R ratio. IEC 60909 estimates it as

|  | ip=κ2 Ik″, κ≈1.02+0.98 e−3R/X | (8.22) |
| --- | --- | --- |

so that for X/R=15 the peak is 1.822=2.58 times the symmetrical RMS value [16]. A limiter intended to relieve breaker making duty or semiconductor stress must therefore be checked in the time domain.

#### Example 8.12. Required limiter impedance and peak current

A 33 kV system has a per-phase Thevenin impedance of 0.127+j1.90 Ω (X/R=15). Find the additional reactance that reduces the symmetrical three-phase fault current to 5 kA, and compare the first peaks with and without the limiter.

Solution. Vph=33/3=19.05 kV. Neglecting R, Xtot=19.05/5=3.81 Ω and Xlim=3.81−1.90=1.91 Ω. Without the limiter Ik″=19.05/1.904=10.0 kA and ip=1.822×10.0=25.7 kA. With a reactive limiter the X/R ratio of the loop rises to about 30, so κ≈1.91 and ip≈1.912×5.0=13.5 kA. Limiter insertion transients, breaker recovery voltage and energy duty still require an EMT study.

### 8.5.2 Series-resonant SSFCL

The simplest SSCL places a reactor L1 in series with a capacitor C1 tuned to the fundamental, ω2L1C1=1, so that in normal operation the series impedance is nearly zero (Figure 8.25). A GTO or thyristor switch across C1 closes within about 3 ms when a fault is detected, removing the capacitor and leaving XL1 in the circuit. An MOV across the capacitor limits its overvoltage while the switch closes, and a small reactor in the bypass limits the capacitor discharge current. Figure 8.26 shows a simulated 11 kV, 50 Hz case: the prospective peak of 16.3 kA is held to about 4.1 kA.

Figure 8.25. Series-resonant solid-state fault current limiter.

Figure 8.26. Simulated fault current without limiter and with a series-resonant SSFCL (L1=10 mH, C1=1013 μF, 11 kV, 50 Hz, fault at 40 ms).

### 8.5.3 Bridge-type and transformer-coupled limiters

In the bridge-type SSCL (Figure 8.27), a diode or thyristor bridge in series with each phase carries a DC reactor Ld biased with a current id larger than the peak load current. In normal operation all bridge arms conduct and the bridge is effectively a short circuit. When a fault drives the line current above id, the bridge forces the line current to equal the reactor current, and Ld appears in series with the line, limiting di/dt to approximately Vm/Ld. Figure 8.28 shows the line and reactor currents. The DC reactor current ratchets upward each half cycle, so a downstream breaker, or gate blocking of the thyristors, must clear the fault within a few cycles.

Figure 8.27. Single-phase bridge-type SSCL with DC reactor.

Figure 8.28. Simulated line and DC-reactor currents of a bridge-type SSCL during a fault at 40 ms.

In the transformer-coupled version, the bridge is connected to the secondary of a series transformer whose primary is in the line. In normal operation the secondary is short-circuited by the thyristors, and the transformer presents only its leakage impedance. On a fault the thyristors are blocked, and the transformer magnetizing impedance, together with a secondary reactor, limits the current. Its control sequence is as important as the power circuit. During start-up the controller verifies voltage magnitude, phase and frequency on both sides, establishes a synchronization reference and energizes the DC reactor before closing the synchronizing path. During a fault the gating is removed or reconfigured, and freewheeling devices provide a path for the reactor energy. Reclosing is permitted only after voltage recovery, phase and frequency checks and confirmation of the bypass state, because an incorrect transition can create severe overvoltage or inrush.

Regardless of topology, the protection sequence has five recognizable states: normal conduction, fault detection, impedance insertion, fault clearing and recovery (Figure 8.29). Detection must be fast but secure. Instantaneous current, di/dt, voltage depression, differential quantities or combinations can be used. A very low threshold risks operation during transformer energization or motor starting; a high threshold sacrifices the first-peak benefit. Coordination with downstream relays and breakers therefore belongs in the limiter design, not in a later protection review.

Figure 8.29. Generic operating sequence of a fast solid-state fault current limiter.

### 8.5.4 Solid-state breakers and transfer switches

A mechanical breaker cannot influence the first current peak, interrupts only at a current zero after several cycles, and tolerates a limited number of full-rated fault interruptions before contact maintenance. A solid-state breaker (SSB) built from GTOs, IGCTs, IGBTs or thyristors with forced commutation interrupts within a fraction of a cycle and without contact wear. SSBs are used for fast load and fault interruption, as fault-current limiters (with a reactor inserted when the switch opens), and as bus-tie breakers that separate a faulted section before its neighbours see a deep sag.

A limiter and a breaker solve different parts of the protection problem: the limiter reduces the magnitude and rate of rise of current, while the breaker establishes isolation. A solid-state transfer switch (SSTS) does neither; it commutates a sensitive load from a failing preferred feeder to an alternate feeder within about a quarter cycle [17]. Thyristor SSTS designs are efficient because they exploit natural current zeros, while fully controllable devices interrupt more freely but need greater semiconductor and surge-energy capability. Hybrid designs keep a mechanical contact in parallel to carry the load current in normal operation, so that the semiconductor conducts only during the transition and its conduction losses are avoided.

### 8.5.5 Comparison with superconducting limiters

A superconducting fault current limiter (SCFCL) presents near-zero impedance until the current exceeds the critical value, at which the superconductor quenches and a high impedance appears. It acts intrinsically, without detection electronics. Its drawbacks are the cryogenic plant and the recovery time after a quench, which ranges from about a second to tens of seconds depending on design and on the energy dissipated. Solid-state limiters reset faster and are fully controllable, but they carry on-state losses in normal operation unless bypassed.

## 8.6 The Thyristor-Controlled Voltage Limiter (TCVL)

### 8.6.1 Metal-oxide varistors

Zinc-oxide varistors protect equipment against overvoltages because their V-I characteristic is extremely nonlinear:

|  | I=kVα ⇔ V=C I1/α | (8.23) |
| --- | --- | --- |

where I is the varistor current, V its voltage, k and C constants of the material and geometry, and α the nonlinearity exponent, typically 20 to 50 for ZnO against about 5 for the older silicon-carbide arresters. Over many decades of current the voltage changes by only a few tens of percent (Figure 8.30). Varistors are rated by their continuous operating voltage, by their residual (clamping) voltage at a specified impulse current, and by the energy or charge they can absorb [18]. The energy limit follows from thermal stability: a block that absorbs too much energy heats, its leakage current rises, and thermal runaway can follow.

Figure 8.30. Normalized V-I characteristics of metal-oxide varistors for several nonlinearity exponents.

The power law is valuable for understanding but not sufficient for arrester design. Manufacturer data specify residual voltage at standardized current impulses, temporary-overvoltage capability and energy withstand. During a transient the absorbed energy is

|  | E=t1t2v(t) i(t) dt | (8.24) |
| --- | --- | --- |

Lowering the clamping level reduces insulation stress but generally increases arrester current and absorbed energy, so TCVL design is an insulation-coordination and thermal problem as much as a voltage-threshold problem.

### 8.6.2 Principle of the TCVL

A gapless MOV arrester is designed so that it does not conduct significantly at the highest continuous voltage; its clamping level is therefore around 1.7 times the normal peak voltage. Many temporary and switching overvoltages that harm equipment lie below that level. The TCVL (Figure 8.31) connects an antiparallel thyristor switch across a lower section of the arrester stack. When an overvoltage is detected, the thyristors short that section, and the remaining section clamps at a lower level:

|  | Vlim=(1−fb) Vclamp | (8.25) |
| --- | --- | --- |

where fb is the fraction of the stack bypassed and Vclamp the clamping voltage of the full stack. The thyristors are fired only for the duration of the disturbance, so the full stack withstands normal voltage continuously. Once the current through the bypass reaches a natural zero after gating stops, the thyristors recover and the full stack resumes the continuous-voltage duty. The reduced protective level is used to limit dynamic overvoltages after load rejection, overvoltages during capacitor energization, and the voltage across series capacitors (Figure 8.32). In a three-phase installation each phase has its own voltage measurement, gate isolation and energy check, so that an unsymmetrical disturbance does not force identical action in all phases.

Figure 8.31. Thyristor-controlled voltage limiter: thyristor switch across a section of an MOV stack.

Figure 8.32. Idealized TCVL action during a temporary overvoltage. The full stack would not conduct below about 1.7 pu; bypassing part of it lowers the limiting level to 1.25 pu only while the thyristors are gated.

A practical controller must distinguish a short surge from a temporary overvoltage that justifies controlled bypass. The trigger can use instantaneous voltage, a filtered envelope, event classification or a combination, and the firing decision must respect thyristor polarity (Figure 8.33). The principal design trade-off is between protective level and energy: bypassing more discs lowers the clamping voltage but forces larger current through the remaining discs and increases their absorbed energy.

Figure 8.33. State sequence of a thyristor-controlled voltage limiter.

#### Example 8.13. MOV energy check

A TCVL clamps a transient at 45 kV while the average arrester current during the main conduction interval is 1.8 kA for 3 ms. Estimate the absorbed energy with a rectangular-pulse approximation.

Solution. E≈VclampIavgΔt=45 000×1 800×0.003=243 kJ. The rectangular approximation is adequate for a first sizing check; final selection should integrate the actual v(t)i(t) waveform with Equation (8.24) and compare it with the manufacturer’s single-event and repetitive energy capability.

#### Example 8.14. TCVL bypass fraction

A full MOV stack has an effective clamping level of 90 kV. A controlled event requires about 63 kV. Using the proportional stack model of Equation (8.25), estimate the fraction of the stack to bypass.

Solution. fb=1−63/90=0.30, so about 30 % of the stack is bypassed. This first-order voltage-sharing model must be confirmed with the actual residual-voltage characteristic, disc tolerances and energy distribution.

### 8.6.3 Capacitor-switching transients

Energizing a capacitor bank through a mechanical switch forms an LC circuit with the source inductance. The inrush oscillates at the natural frequency

|  | f0=12πLC, Z0=LC, Iinrush≈ΔVZ0 | (8.26) |
| --- | --- | --- |

where L is the source inductance, C the bank capacitance, Z0 the characteristic impedance and ΔV the voltage difference at closing. The capacitor voltage can overshoot to 2 pu, or to 3 pu if a charged bank is re-energized at the opposite supply peak. Figure 8.34 shows this worst case, the effect of an MOV clamping at 1.7Vm, and the further reduction obtained when a TCVL lowers the clamping level to 1.3Vm. The energy the MOV must absorb is the integral of vi over the clamping intervals, and it grows sharply as the clamping level is lowered, which is the main design trade-off.

Figure 8.34. Re-energization of a capacitor bank charged to −Vm: no limiter, MOV clamping at 1.7Vm, and TCVL clamping at 1.3Vm (normalized, natural frequency eight times fundamental, damping neglected).

### 8.6.4 Protection coordination and limitations

TCVL action must be coordinated with conventional surge arresters, breaker switching, capacitor discharge devices and insulation withstand. Triggering too early increases MOV energy and thyristor duty; triggering too late sacrifices the insulation benefit. The device is most attractive where a temporarily lower protective level is valuable but cannot be tolerated continuously because of leakage current and thermal constraints.

## 8.7 Comparison and Selection

The technologies in this chapter should not be ranked on a single scale. UPFC and IPFC are power-flow controllers; TCPAR and TCVR are specialized regulators; the IPC is principally a passive network-shaping device; SSCL and SSB are protection devices; the TCVL is an insulation-protection device. Table 8.1 summarizes their attributes.

Table 8.1. Comparison of the controllers of this chapter.

| Attribute | UPFC | IPFC / GUPFC | TCPAR / TCVR | IPC / APST | SSCL / SSB | TCVL |
| --- | --- | --- | --- | --- | --- | --- |
| Parameters controlled | V, Xeff, δeff | Flows in several lines | Angle or magnitude | Shape of P-δ curve | Fault current | Overvoltage level |
| Independent P and Q | Yes | Yes in prime line | No | No (passive) | Not applicable | Not applicable |
| Power stage | Two VSCs | n VSCs (plus shunt in GUPFC) | Thyristor tap-changer or VSC | Reactors, capacitors, transformers | Thyristors/GTOs/IGBTs and reactors | Thyristors and MOV |
| External real-power port | Yes, shunt VSC | No in pure IPFC | Not needed (transformer type) | None | Not a dispatch device | None |
| Speed | Sub-cycle | Sub-cycle | About one cycle (thyristor) | Inherent | 1 to 3 ms | Sub-cycle |
| Harmonics | Low (multi-pulse or multilevel) | Low | Some (phase control) or none (stepped) | None | None in normal state | None |
| Normal-state loss | Converter and transformer loss | Converter loss | Low to moderate | Low | Topology dependent | Very low |
| Main limitation | Cost, losses, two ratings | DC balance, supporting margin | Range set by windings, valve duty | Fixed characteristic, branch circulation | Energy, recovery voltage | MOV energy, thyristor duty |
| Best-fit application | Critical corridor needing fast multi-variable control | Several lines at one substation | Fast loop-flow or voltage regulation | Tie with short-circuit constraint | Excess fault level, fast isolation | Dynamic insulation coordination |

Selection should begin with the constrained state variable, not with the device name: active power, reactive power, voltage magnitude, phase angle, fault current or transient overvoltage. The next layer is the dynamic requirement: steady-state dispatch, electromechanical damping, sub-cycle protection or insulation coordination. Only then should topology, rating, redundancy, loss and cost be compared. A UPFC is the most general controller in this chapter, but it is not automatically the best choice. If the requirement is only slow loop-flow control, a phase-shifting transformer may provide the service with much lower loss and complexity. If several lines at one substation must exchange controllable real power, the IPFC is structurally better matched. If short-circuit level is the binding constraint, neither a UPFC nor an IPFC substitutes for a properly designed fault current limiter, and if insulation stress from a switching event is the problem, a TCVL addresses a different physical quantity altogether.

A second useful distinction is the energy path. The UPFC has an AC real-power port through its shunt converter. A pure IPFC redistributes real power among series converters but has no external real-power source. The IPC needs no semiconductor DC link. SSCL and TCVL are designed around transient energy and protection duty. Figure 8.35 places the devices on a qualitative map of response speed and steady-state controllability.

Figure 8.35. Qualitative map of response speed and steady-state power-flow controllability. Positions are indicative only and must not be read as equipment ratings.

#### Example 8.15. Selecting the controller by the binding constraint

A substation has three outgoing lines. One line is overloaded, a second has spare transfer capability, bus voltage is acceptable, and the short-circuit level is already close to the breaker rating. Which controller family is the natural first candidate if the objective is to redistribute steady line flows without increasing bus fault contribution?

Solution. An IPFC (or a set of SSSCs, if real-power exchange between lines is not needed) is the natural FACTS candidate. Its series converters reshape line flows directly, the common DC link lets it exchange real power among lines, and, unlike a shunt converter, series converters behind a fast bypass add little to the bus fault level. A UPFC could control one corridor strongly but does not coordinate several lines, and its shunt converter contributes fault current. The final decision still requires a short-circuit and protection study.

## 8.8 Recent Advances and Research Directions

The research question has moved from whether these controllers can regulate power flow to how they should be built, dispatched, stabilized and protected in networks dominated by power electronics. This section surveys the state of the art and develops each research direction from an equation or constraint already introduced in Sections 8.1 to 8.6, so that a research scholar can see precisely which part of the classical model a new contribution must change. Each subsection follows the same pattern: what has been achieved, the governing relations, the limitations of current approaches, and the open problems worth pursuing.

### 8.8.1 State of the art: from multi-pulse GTO converters to modular controllers

The first generation of combined controllers, represented by Inez (1998) and Marcy (2001 to 2004), used GTO converters whose output was synthesized by multi-pulse magnetic summation [6], [11], [7]. The transformers were large, the losses were a few percent of rating, and the converter could not be partitioned easily for redundancy. Three developments have since changed the picture (Figure 8.36).

Figure 8.36. Milestones in combined and special-purpose FACTS controllers, from concept to modular and solid-state implementations.

The first is the modular multilevel converter (MMC). The 220 kV Nanjing West Ring UPFC, commissioned in 2015, was the first MMC-based UPFC: one shunt converter on the 35 kV tertiary of a 220 kV transformer and two series converters in two parallel 220 kV lines, which makes it a GUPFC-type arrangement in the terminology of Section 8.2.3. The 500 kV UPFC in the southern Suzhou grid entered service at the end of 2017 and was, at that time, the highest-voltage and largest-capacity UPFC in operation [19]. MMC cells replace the multi-pulse transformers, provide near-sinusoidal output without filters, and allow redundant cells to be added at modest cost.

The second is the move toward transformerless and distributed series injection. Divan and Johal proposed distributed FACTS, in which many small, line-mounted modules each inject a modest series voltage [20]; the concept matured into commercial modular SSSCs that are now installed by transmission owners in Europe and the Americas to push power off overloaded circuits [21]. At distribution and medium voltage, a transformerless UPFC built from two cascaded multilevel inverters was demonstrated on a 4.16 kV test system [22].

The third is solid-state isolation. Recent work replaces line-frequency insertion transformers by cascaded modules with high-frequency isolated DC-DC stages (dual-active-bridge cells), so that the series and shunt ports exchange energy through compact medium-frequency magnetics [23]. Direct-injection low-voltage controllers that avoid transformers altogether and process only part of the line power have also been proposed for feeders with high penetration of distributed generation [24]. Reviews of the wider FACTS field confirm that UPFC, IPFC, distributed power-flow control and fault-current limitation remain active areas, with growing attention to optimal placement and stability in renewable-rich grids [15], [25].

Table 8.2. Representative field installations and demonstrators discussed in this chapter.

| Year | Installation | Voltage level | Technology | Significance |
| --- | --- | --- | --- | --- |
| 1998 | Inez UPFC, AEP, USA | 138 kV | Two ±160 MVA GTO multi-pulse VSCs | First full-scale UPFC; STATCOM, SSSC and UPFC modes [6], [7] |
| 1998 | Plattsburgh APST, NYPA, USA | Tie to Vermont | Inductors in parallel with an existing PAR | First commercial IPC-family device [14] |
| 2001 to 2004 | Marcy CSC, NYPA, USA | 345 kV | Two 100 MVA VSCs, one shunt and two series transformers | Convertible STATCOM, SSSC, UPFC and IPFC [11] |
| 2015 | Nanjing West Ring, China | 220 kV | Three MMCs, two series and one shunt | First MMC-based UPFC [19] |
| 2017 | Southern Suzhou, China | 500 kV | MMC-based UPFC | Highest voltage UPFC at commissioning [19] |
| 2016 | Transformerless UPFC test system, USA | 4.16 kV | Two cascaded multilevel inverters | Removes insertion and shunt transformers [22] |
| 2020s | Modular SSSC fleets, several utilities | 110 kV to 230 kV class | Line- or substation-mounted single-phase modules | Relocatable, incremental series compensation [20], [21] |

### 8.8.2 Modular multilevel and solid-state UPFC architectures

For a modular series converter with N cells whose fundamental outputs are aligned, the commanded series voltage is the phasor sum

|  | Vse=k=1NVk | (8.27) |
| --- | --- | --- |

Equal sharing gives Vk=Vse/N only while every cell has the same available voltage and thermal margin. If nb cells are bypassed after failures, the survivors must raise their contribution, and the design condition becomes

|  | VseN−nb≤Vcell,max ⇒ N≥VseVcell,max+nb | (8.28) |
| --- | --- | --- |

Figure 8.37(a) shows how quickly the per-cell requirement rises when the cell count is small. Cell voltage is not the only constraint. Each cell of a series converter carries the full line current, and in a single-phase H-bridge cell the instantaneous power contains a component at twice the line frequency. With RMS cell voltage V, RMS current I and phase angle φ between them,

p(t)=VIcosφ−VIcos(2ωt−φ)

so the stored energy oscillates with a peak-to-peak value ΔE=Scell/ω, where Scell=VI. Since ΔE≈C Vdc ΔVpp, the cell capacitance needed to hold the peak-to-peak ripple to ΔVpp is

|  | Ccell≥Scellω Vdc ΔVpp | (8.29) |
| --- | --- | --- |

This relation explains why single-phase modular series converters are capacitor-dominated in volume and why ripple-cancelling arrangements, such as three-phase cell groups or active power decoupling, are attractive research topics.

Redundancy is usually expressed as availability. If Nr cells are required, r redundant cells are installed and each cell has availability Ac with independent failures, the converter is available whenever no more than r cells are out:

|  | Asys=k=0rNr+rk(1−Ac)kAc Nr+r−k | (8.30) |
| --- | --- | --- |

Figure 8.37(b) shows that a single redundant cell typically reduces unavailability by more than an order of magnitude.

Figure 8.37. Modular series converters: (a) required cell voltage after bypass for an 18 kV injection and (b) converter unavailability versus cell availability for 12 required cells with 0, 1 and 2 redundant cells.

#### Example 8.16. N-1 voltage margin of a modular UPFC

A modular series converter contains six identical cells, each rated for 4 kV fundamental output, and the operating point requires 18 kV of injection. Find the per-cell voltage before and after one cell is bypassed, and the minimum cell count for operation with two cells bypassed.

Solution. Normal sharing is 18/6=3.0 kV per cell. After one bypass the five survivors supply 18/5=3.6 kV each, leaving 0.4 kV of margin per cell. With two bypassed cells, Equation (8.28) gives N≥18/4+2=6.5, so seven cells are required.

#### Example 8.17. Cell capacitor sizing

A single-phase H-bridge cell of a modular SSSC injects 1.2 kV RMS into a line carrying 1.0 kA RMS at 50 Hz. Its DC voltage is 2.0 kV and the peak-to-peak ripple must not exceed 10 %. Find the minimum cell capacitance. Then find the converter availability if 12 such cells are required, one redundant cell is fitted and each cell has Ac=0.995.

Solution. Scell=1.2×1.0=1.2 MVA and ΔVpp=200 V, so Equation (8.29) gives C≥1.2×106/(314.16×2000×200)=9.55 mF. Without redundancy Asys=0.99512=0.9416. With one redundant cell, Equation (8.30) gives Asys=0.99513+13×0.005×0.99512=0.9981, so the unavailability falls from 5.8 % to 0.19 %.

The principal limitations of current architectures are three. Series cells see the full line fault current, so their bypass must act within the first current rise. Floating cells must be insulated to line potential and supplied with gate power. Solid-state designs with medium-frequency isolation add two conversion stages, so their efficiency and fault ride-through have yet to be proven at transmission ratings [23]. Open problems include fault-tolerant capacitor-voltage balancing under unequal cell temperatures, ripple-energy reduction, wide-bandgap cells for medium-voltage series injection, and reliability models that combine cell failure rates with bypass-switch failure modes.

### 8.8.3 Distributed and modular series power-flow control

A modular SSSC injects a voltage in quadrature with the line current, Vm=±jXmI, so each module emulates a small positive or negative reactance and n modules emulate ΔX=nXm [20], [21]. For two parallel paths of reactance X1 and X2 carrying a total PT, adding ΔX to path 1 gives

|  | P1=PT X2X1+X2+ΔX, P2=PT−P1 | (8.31) |
| --- | --- | --- |

provided the external network holds PT. The attraction is incremental deployment: modules can be added, removed or relocated as congestion patterns change. The limitations follow from the physics. A quadrature-only module exchanges no real power, so it cannot emulate resistance or move power against the natural angle in the way a UPFC can. Each module must bypass itself during faults, and a fleet of modules changes the apparent impedance seen by distance relays (Section 8.8.8).

#### Example 8.18. Sizing a fleet of series modules

Two parallel paths of 0.3 pu and 0.6 pu share 2.3 pu (natural sharing 1.533 pu and 0.767 pu). Each series module emulates 0.02 pu of inductive reactance. How many modules must be placed in path 1 to reduce its flow to 1.3 pu or less, and what voltage does each module inject?

Solution. From Equation (8.31), 0.9+ΔX≥2.3×0.6/1.3=1.0615, so ΔX≥0.1615 pu and nine modules are needed (ΔX=0.18 pu). Then P1=2.3×0.6/1.08=1.278 pu and P2=1.022 pu. Each module injects Vm=XmI1≈0.02×1.278=0.026 pu, a small voltage that is the basis of the low module rating.

### 8.8.4 Coordinated dispatch and optimal placement

Distributed and combined controllers turn a device-design problem into a constrained network-optimization problem. For branch k between buses i and j with series impedance Zk and a controllable series source Vse,k,

|  | Ik=Vi+Vse,k−VjZk | (8.32) |
| --- | --- | --- |

and an AC optimal power flow with power-flow controllers can be written as

|  | minx,u F(x,u) s.t. g(x,u)=0, h(x,u)≤0, ​Vse,k​≤Vse,kmax, ​Ik​≤Ikmax | (8.33) |
| --- | --- | --- |

where x collects bus voltages, u the generator set points and controller injections, g the AC power-balance equations and h the operating limits. Device-specific couplings are then added. For an IPFC, k​Re(Vse,kIk*)+Ploss=0 from Equation (8.9). For a UPFC, Re(VseI*)+Psh+Ploss=0 together with the shunt limit of Equation (8.6).

The bilinear power term Re(VseI*) makes the problem nonconvex even where the network part is relaxed. Second-order-cone and semidefinite relaxations of the network equations [26], McCormick envelopes for the bilinear device terms, and mixed-integer formulations for placement are the standard tools; learning-based surrogates are increasingly used to screen many contingencies quickly. A recurring weakness of published work is that the OPF may return an injection inside the ideal control disk that violates the converter current limit in a contingency. A credible formulation enforces converter capability in every post-contingency state, not only in the base case. Security-constrained dispatch of mixed fleets (UPFC, PST and modular SSSC together), stochastic formulations for renewable variability, and exactness conditions for relaxations that include device constraints remain open.

### 8.8.5 Converter-grid interaction and impedance-based stability

Fast converter controls give a converter port a frequency-dependent terminal impedance. A controller that behaves well in one network can interact with another converter, an HVDC station or a weak or resonant network through the PLL, current controller, DC link and outer loops [27]. Represent the converter port by an impedance Zc(s) and the network seen from it by Zg(s). For a current-controlled port the interaction is governed by the minor-loop gain

|  | L(s)=Zg(s)Zc(s)=Zg(s) Yc(s) | (8.34) |
| --- | --- | --- |

and the interconnection is stable if L(s) satisfies the Nyquist criterion, given that each subsystem is stable on its own [28]. In practice the magnitude crossover ​Zg​=​Zc​ is located and the phase margin PM=180∘−​∠Zg−∠Zc​ is evaluated there. For three-phase studies the scalar test is replaced by the generalized Nyquist criterion applied to dq-frame or sequence-domain matrices,

|  | detI+Zg(s) Yc(s)=0 | (8.35) |
| --- | --- | --- |

whose roots are the closed-loop interaction modes.

A minimal model that already shows the mechanism is a current-controlled VSC with filter inductance Lf, proportional current gain Kp and a computation-plus-PWM delay Td:

|  | Zc(jω)=jωLf+Kp e−jωTd | (8.36) |
| --- | --- | --- |

Its real part KpcosωTd becomes negative above f=1/(4Td). In that band the converter port is an active, negative-resistance source, and any network inductance that crosses its magnitude there leaves little phase margin (Figure 8.38). For a UPFC the problem is multi-port: a perturbation at the shunt terminal modulates Vdc, which changes the voltage available to the series port. Deriving the two converters separately and joining them through an ideal, infinitely stiff DC source hides exactly this coupling, which is one reason three-port impedance models of combined controllers are a worthwhile research topic.

Figure 8.38. Impedance-based screening for the converter model of Equation (8.36) (Lf=1 mH, Kp=15 Ω, Td=150 μs) against two network inductances. The stiffer network crosses inside the negative-resistance band and has a much smaller phase margin.

#### Example 8.19. Phase-margin screen

For the converter of Figure 8.38, find the frequency above which the port becomes active, and compare the interaction margins for Lg=0.5 mH and Lg=2 mH (Rg=0.05 Ω).

Solution. 1/(4Td)=1/(4×150×10−6)=1667 Hz. Solving ​Zg​=​Zc​ numerically gives a crossover at 903 Hz for Lg=2 mH, where ∠Zc≈−30∘, ∠Zg≈+90∘ and PM≈61∘. For Lg=0.5 mH the crossover moves to 1598 Hz, close to the active band, where ∠Zc≈−78∘ and PM≈12∘, a poorly damped harmonic resonance. The result shows that “stronger” is not always “safer” for delay-dominated interactions, and it identifies the frequency at which an EMT study should look first.

### 8.8.6 Wide-area damping control and communication delay

Supplementary damping loops on a UPFC or IPFC are increasingly driven by remote phasor measurements. The communication and processing delay Td adds a phase lag

|  | ϕd=−360 f Td degrees, e−sTd≈1−sTd/21+sTd/2 | (8.37) |
| --- | --- | --- |

at the mode frequency f; the first-order Padé form on the right is used when the delay must appear in a state-space model. A delay that looks small in milliseconds can consume much of the phase lead designed into a damping controller (Figure 8.39). If the uncompensated lag rotates the damping torque far enough, a loop designed to damp a mode can excite it.

Figure 8.39. Phase lag introduced by end-to-end delay in a wide-area damping loop.

#### Example 8.20. Communication delay in supplementary damping

A wide-area UPFC damping loop acts on a 0.8 Hz inter-area mode. Find the phase lag caused by delays of 40 ms and 120 ms.

Solution. ϕd=−360×0.8×0.040=−11.5∘ and −360×0.8×0.120=−34.6∘. The second value is comparable to the lead normally provided by one compensation stage, so delay must be included in the design and its worst-case value used in robustness checks.

Research directions here include delay-robust and adaptive damping controllers, coordination of several FACTS damping loops so that they do not compete for the same mode, and cyber-physical resilience when measurements are lost or spoofed.

### 8.8.7 Grid-forming concepts and current-limited operation

A conventional UPFC is synchronized to the network through a PLL and regulates power flow; it does not establish frequency. Grid-forming control is now central to converter-dominated systems, and a combined controller could in principle let its shunt port form a local voltage angle while the series port shapes corridor flow. The difficulty is energy and current coordination. Both ports draw on one DC store and on semiconductor current limits, and during a fault the shunt port’s apparent-power capability shrinks with the voltage:

|  | Psh2+Qsh2≤VIsh,max2 ⇒ ​Qsh​≤VIsh,max2−Psh2 | (8.38) |
| --- | --- | --- |

Once the current limit is active, the pre-fault P-Q references cannot all be satisfied, and the priority rule decides the outcome (Figure 8.40). Grid-forming literature shows that the choice among current-reference saturation, virtual impedance and voltage limiting changes fault contribution, synchronization stability and recovery [29]. For a virtual-impedance limiter with internal voltage E and a worst-case terminal voltage Vmin, the impedance needed to respect the current limit is ​Zv​≥(E−Vmin)/Imax.

Figure 8.40. Shunt-converter capability at normal and depressed voltage with 0.3 pu of real power reserved for DC-link support.

#### Example 8.21. Reactive capability during a voltage dip

A UPFC shunt converter has Ish,max=1.0 pu and must keep drawing 0.3 pu of real power to support the series converter. Find its reactive capability at V=1.0 pu and during a fault that depresses the bus to 0.5 pu.

Solution. From Equation (8.38), ​Qsh​≤1−0.09=0.954 pu at 1.0 pu voltage, and ​Qsh​≤0.25−0.09=0.400 pu at 0.5 pu. The dip removes 58 % of the reactive support exactly when it is most needed, unless the series converter is bypassed so that the real-power reservation can be released. A study should state this priority explicitly.

### 8.8.8 Protection-aware design and solid-state interruption

Series and combined controllers change the voltages and currents measured by distance, differential and overcurrent protection. Let a series source inject Vinj between the relay location and the line, so that the line-side voltage is Vrelay+Vinj. For a bolted fault at a fraction m of a line of impedance ZL,

|  | Zapp=VrelayI=mZL−VinjI | (8.39) |
| --- | --- | --- |

Capacitive emulation (Vinj=+jXcI) shortens the apparent impedance and makes zone 1 overreach; inductive emulation makes it underreach. Because the converter saturates, blocks and bypasses during the fault, Vinj itself changes within the relay measurement window, so the study must reproduce those transitions rather than assume instantaneous removal of the controller.

#### Example 8.22. Distance-relay overreach

A line has ZL=j0.50 pu and a zone-1 reach of 80 % (j0.40 pu). A series converter between the relay and the line emulates 0.15 pu of capacitive reactance during the fault. Up to what fraction of the line does zone 1 now operate?

Solution. From Equation (8.39), Zapp=j(0.50m−0.15). Zone 1 operates while 0.50m−0.15≤0.40, that is, for m≤1.10. Zone 1 now reaches 10 % into the adjacent line, so either the reach must be reduced while the converter is active or the converter must bypass before the zone-1 decision is made.

Solid-state interruption raises a related energy problem. When a semiconductor breaker turns off current I0 in a loop of inductance L against a driving voltage Vs, the current commutates into a surge arrester clamping at Vc=kVs. The current then falls linearly, and

|  | tf=LI0Vc−Vs, EMOV=12LI02 kk−1 | (8.40) |
| --- | --- | --- |

so a low clamping ratio shortens neither the stress nor the energy: both the fall time and the absorbed energy grow without bound as k→1 (Figure 8.41). The same trade-off between clamping level and energy governs the TCVL (Section 8.6.2), and it is why hybrid breakers, which combine a mechanical path with a semiconductor commutation branch, are the preferred architecture for HVDC grids [30].

Figure 8.41. Normalized MOV energy and current fall time of a solid-state breaker versus clamping ratio.

#### Example 8.23. Solid-state breaker energy

A semiconductor breaker interrupts 5 kA in a 10 kV DC feeder with 1 mH of loop inductance. The arrester clamps at 15 kV. Find the current fall time and the energy the arrester absorbs.

Solution. k=1.5, so tf=10−3×5000/(15 000−10 000)=1.0 ms and EMOV=0.5×10−3×50002×1.5/0.5=37.5 kJ, three times the magnetic energy stored in the loop.

### 8.8.9 Data-driven methods and digital twins

Machine learning is most defensible here as a computational aid that accelerates a physics-constrained task: estimating uncertain parameters, screening many contingencies, constructing an OPF surrogate, detecting oscillatory modes or predicting converter thermal margin. The network equations and converter capability limits should remain explicit. A common way to keep a learned model physically consistent is to penalize violations of the governing equations during training:

|  | L=Ldata+λ1g(x,u)2+λ2i​max0,hi(x,u)2 | (8.41) |
| --- | --- | --- |

where g and h are the equality and inequality constraints of Equation (8.33). Even then, a learned controller that violates Vse,max, converter current, DC-link energy or arrester energy is not physically valid, however small its training error. A digital twin of a UPFC or IPFC corridor should state what it synchronizes (line parameters, transformer data, converter loss coefficients, capacitor condition, valve temperature, protection status), which decision improves because of that synchronization, and over what operating range the model has been validated against measurements. Its contribution should be judged by measurable improvement in prediction, control or maintenance, not by the label.

### 8.8.10 Validation hierarchy and publishable evidence

A research claim must be matched to a model that preserves the phenomenon being claimed (Figure 8.42). Power-flow redistribution can be established with a validated steady-state model. Oscillation damping needs eigenvalue or time-domain evidence over several operating points. Harmonic, switching and impedance-interaction claims require EMT or switching models. Fault-current, bypass and relay claims require EMT with protection logic. Claims about implementation delay, sampling and gate logic are strongest when supported by controller or protection hardware-in-the-loop tests. A sound workflow is therefore to derive the reduced model, identify the expected mechanism, test sensitivity analytically, verify with EMT, and move to HIL only for claims that depend on real controller or relay timing. This avoids both extremes: a very detailed model used without understanding the mechanism, and implementation claims drawn from an oversimplified model.

Figure 8.42. Model hierarchy for research on combined and special-purpose FACTS controllers. Fidelity increases from steady-state dispatch to switching, protection and hardware validation.

### 8.8.11 Open problems and potential contributions

Table 8.3 links each open problem to the equation it modifies, the reason current methods fall short, a contribution that would be publishable, and the evidence a reviewer will expect.

Table 8.3. Research map for combined and special-purpose FACTS controllers.

| Research problem | Governing relation | Limitation of current practice | Potential contribution | Minimum evidence |
| --- | --- | --- | --- | --- |
| Fault-tolerant modular series converters | Equation (8.28), Equation (8.29), Equation (8.30) | Equal-sharing assumptions; ripple energy sizes the cells | Thermal-aware balancing, ripple cancellation, wide-bandgap cells | Switching model, loss and reliability analysis, prototype |
| Security-constrained dispatch of mixed fleets | Equation (8.32), Equation (8.33) | Converter limits checked only in the base case | Contingency-aware formulations with exactness guarantees | Benchmark networks, N-1 validation, solver statistics |
| Multi-port interaction of UPFC and IPFC | Equation (8.35) with DC-link coupling | Converters modelled separately with a stiff DC source | Three-port impedance models and design rules | Frequency scans validated against EMT |
| Delay-robust wide-area damping | Equation (8.37) | Fixed-delay designs; no coordination among devices | Robust or adaptive coordinated damping | Eigenvalue studies, real-time HIL with delay |
| Grid-forming combined controllers | Equation (8.38), Equation (8.7) | Priority rules unstated; DC energy shared implicitly | Current-limited dual-port control with explicit priority | EMT fault studies, synchronization-stability analysis |
| Protection with series injection | Equation (8.39) | Instantaneous bypass assumed in relay studies | Adaptive relay settings, converter-aware protection logic | EMT plus protection HIL |
| Energy-aware solid-state limiters and breakers | Equation (8.40), Equation (8.24) | Current peak or clamp level optimized alone | Co-design of clamp level, MOV energy and recovery | EMT, thermal model, high-power test |
| Physics-constrained learning | Equation (8.41) | Black-box models extrapolate poorly | Hybrid models with certified constraint satisfaction | Out-of-distribution tests, constraint-violation statistics |

The industrial relevance is direct. Transmission owners need incremental, relocatable ways to release capacity faster than new lines can be built, and every item in Table 8.3 either lowers the cost of such control, makes it safer to operate, or makes its benefit easier to prove to a regulator.

## Key Equations

Table 8.4. Key equations of Chapter 8.

| Equation | Expression | Conditions |
| --- | --- | --- |
| (8.2) | Pr=VsVrXsinδ+VrVpqXsin(δ+ρ) | UPFC at sending end, ρ measured from Vs |
| (8.3) | (Pr−P0)2+(Qr−Q0)2=(VVpq/X)2 | Control circle, Vs=Vr=V |
| (8.5) | Psh+Pse=0 | Lossless UPFC, steady state |
| (8.7) | ddt12CdcVdc2=−(Psh+Pse+Ploss) | DC-link dynamics |
| (8.10) | P1pq+P2pq=0 | Two-converter IPFC |
| (8.11) | ​V2q​≤V2,max2−V2p2 | Supporting-converter margin |
| (8.13) | ​Vσ​=2Vssin(σ/2) | Ideal phase shifter |
| (8.14) | P=V2Xsin(δ±σ) | Phase shifter on a lossless line |
| (8.15) | N=3L, ΔVmax=3L−12Vstep | Ternary windings |
| (8.18) | P=PmaxcosδSR−ψ1+ψ22sinψ2−ψ12 | IPC, ​B1​=​B2​ |
| (8.21) | Xlim=Vph/If,lim−Xs | Limiting reactance, inductive source |
| (8.22) | ip=κ2Ik″, κ≈1.02+0.98e−3R/X | First fault-current peak |
| (8.23) | I=kVα | Metal-oxide varistor |
| (8.25) | Vlim=(1−fb)Vclamp | TCVL |
| (8.26) | f0=1/(2πLC), I≈ΔV/Z0 | Capacitor energization |
| (8.28) | N≥Vse/Vcell,max+nb | Modular converter with bypassed cells |
| (8.29) | Ccell≥Scell/(ωVdcΔVpp) | Single-phase cell ripple |
| (8.34) | L(s)=Zg(s)/Zc(s) | Impedance-based stability |
| (8.38) | ​Qsh​≤(VIsh,max)2−Psh2 | Current-limited shunt port |
| (8.39) | Zapp=mZL−Vinj/I | Relay with series injection |
| (8.40) | EMOV=12LI02 k/(k−1) | Solid-state interruption |

## Common Misconceptions

- “The UPFC’s DC link carries the reactive power of the series converter.” Only real power, plus losses, passes through the link. The reactive power of each converter is generated internally at its AC terminals.

- “An IPFC can supply net real power to all its lines from the DC capacitor.” A capacitor is not a continuous energy source. Without storage or a shunt real-power port, the series-converter real powers must balance apart from losses.

- “A phase shifter raises the maximum power of a line.” An ideal phase shifter shifts the power-angle curve sideways. It raises the power at a given network angle, but the peak V2/X is unchanged.

- “A quadrature booster is an ideal phase shifter.” A quadrature injection changes both angle and magnitude. An ideal phase shifter preserves magnitude by a different phasor geometry and needs a slightly different injection.

- “A capacitor in parallel with a PST carries power in the same direction as the PST.” A capacitive branch has negative reactance, so at a positive angle it carries power in the opposite direction. That is exactly what flattens the IPC characteristic.

- “A current limiter replaces the breaker.” A limiter changes the current trajectory; the breaker (or an SSB) still establishes isolation. Hybrid devices may combine both functions, but their ratings and timing requirements remain distinct.

- “Lowering the clamping level is free.” The energy the varistor absorbs rises steeply as the clamping level falls, which is why a TCVL bypasses part of the stack only for the duration of a disturbance.

- “A controller that can set P and Q always improves damping.” The sign and phase of the supplementary path, measurement delay, current limiting and the operating point decide whether a mode is damped or excited.

## Chapter Summary

The UPFC injects a series voltage of any magnitude and phase, supplied with real power by a shunt converter through a common DC link, so it can move the operating point of a line anywhere inside a circle of radius VVpq,max/X around its uncompensated point. Its practical region is the part of that disk that satisfies converter current, voltage and DC-energy limits. The IPFC extends the idea to several lines, transferring real power between them under a single DC-balance constraint that also consumes part of each supporting converter’s voltage margin; generalized and convertible arrangements extend it further. Thyristor-controlled voltage and phase-angle regulators provide fast magnitude or angle control with tap-changer windings, continuously with phase control or in ternary steps. The IPC flattens the power-angle characteristic of a tie and limits its fault contribution with passive components alone. Solid-state current limiters, breakers and transfer switches insert impedance or interrupt current within milliseconds, and the thyristor-controlled voltage limiter lowers the protective level of a varistor stack only when needed. Present research concentrates on modular and solid-state converters, coordinated dispatch, impedance-based stability, current-limited and grid-forming operation, and protection-aware design, each of which modifies a specific equation of the classical theory.

## Solved Numerical Practice Problems

Unless stated otherwise, per-unit quantities use a common three-phase base, line-to-line kilovolts and ohms give three-phase megawatts directly when both end voltages are balanced line-to-line RMS values, trigonometric angles are in degrees, and the UPFC injection angle ρ is measured from the sending-end voltage. Lossless formulas are not applied to problems that include line resistance.

#### Example 8.24. UPFC uncompensated point and control circle

A UPFC is installed on a lossless line with Vs=Vr=1 pu, X=0.5 pu, δ=30∘ and Vpq,max=0.25 pu. Find (a) P0; (b) Q0; (c) the total reactive power absorbed by the line; (d) the centre and radius of the control circle; (e) the range of Pr.

Solution. (a) P0=2sin30∘=1.0 pu. (b) Q0=−2(1−cos30∘)=−0.268 pu. (c) ​I​=2sin15∘/0.5=1.035 pu, so I2X=0.536 pu, half supplied by each end. (d) Centre (1.0,−0.268), radius 0.25/0.5=0.5 pu. (e) 0.5 to 1.5 pu.

#### Example 8.25. Maximum and minimum power and converter duty

For Example 8.24 find (a) ρ for maximum power; (b) Pr and Qr; (c) the line current; (d) the series-converter real and reactive power; (e) the same quantities at minimum power.

Solution. (a) sin(δ+ρ)=1, so ρ=60∘. (b) Pr=1.5 pu and Qr=−0.268 pu (unchanged). (c) From Equation (8.1), I=1.524∠10.13∘ pu. (d) Sse=VpqI*: Pse=0.067 pu, Qse=0.375 pu, ​Sse​=0.381 pu. (e) ρ=240∘: Pr=0.5 pu, Qr=−0.268 pu, I=0.567 pu, Pse=−0.067 pu, Qse=−0.125 pu. The real power through the link is small in both cases; the series-converter rating is governed by VpqI, which depends on the line current as well as on the injected voltage.

#### Example 8.26. Two injection angles for the same active power

On the line of Example 8.24, Vpq=0.45 pu and the target is Pr=1.4 pu. Find (a) both values of ρ; (b) Qr for each; (c) the currents; (d) the series-converter apparent powers; (e) the better choice.

Solution. (a) sin(30∘+ρ)=0.4/0.9, so ρ=−3.61∘ or 123.61∘. (b) Qr=+0.538 pu or −1.074 pu. (c) 1.500 pu or 1.765 pu. (d) 0.675 pu or 0.794 pu. (e) The first: it delivers reactive power to the receiving end with less current and less converter duty.

#### Example 8.27. UPFC on a line with resistance

A 132 kV line has X=175 Ω and R=70 Ω, with equal end voltages at δ=45∘. The UPFC can inject up to 45 kV (line-to-line equivalent). Find (a) P, Qr and current without the UPFC; (b) the maximum receiving-end power and the injection angle; (c) the minimum injection that raises power by 50 % when placed at its best angle.

Solution. The exact complex calculation with Z=70+j175 Ω gives: (a) P0=50.64 MW, Qr=−49.42 Mvar and I0=309.5 A. (b) Optimizing ρ gives Pmax=82.15 MW at ρ=23.2∘, an increase of 62 %, with I=419.3 A. (c) Vpq=36.15 kV line-to-line. Approximate formulas that ignore R, or that force the injection into quadrature, overestimate the voltage needed.

#### Example 8.28. Power transfer at zero angle

With Vs=Vr=1 pu, X=0.5 pu, δ=0 and Vpq=0.4 pu, find (a) the uncompensated power; (b) Pr and Qr at ρ=90∘; (c) the current; (d) the series-converter power.

Solution. (a) Zero. (b) Pr=0.4×1/0.5=0.8 pu and Qr=0. (c) 0.8 pu. (d) Pse=0 and Qse=0.32 pu. Series injection alone establishes power transfer where an uncompensated line carries none.

#### Example 8.29. Shunt-converter rating

In Example 8.25(a) the shunt converter must also supply 0.3 pu of reactive power to the bus. Find (a) its real power; (b) its apparent power.

Solution. (a) Psh=−Pse=−0.067 pu, drawn from the bus. (b) 0.0672+0.32=0.307 pu. Shunt converters are normally rated close to the series converter so that they can operate as a STATCOM.

#### Example 8.30. UPFC with unequal end voltages

Vs=1.0 pu, Vr=0.95 pu, X=0.5 pu, δ=25∘, Vpq=0.2 pu and ρ=50∘. Find (a) P0 and Qr without injection; (b) Pr and Qr with it; (c) the effective sending voltage; (d) the series-converter power.

Solution. (a) P0=0.803 pu and Qr0=−0.083 pu. (b) From Equation (8.2), Pr=1.170 pu and Qr=+0.015 pu. (c) ​Vs+Vpq​=1.139∠32.7∘ pu. (d) Pse=0.061 pu and Qse=0.239 pu.

#### Example 8.31. A 138 kV UPFC

A 138 kV line has X=80 Ω and operates at 35∘; the UPFC can inject 28 kV. Find (a) P0; (b) the UPFC power term; (c) the power range; (d) ρ for 180 MW.

Solution. (a) 1382sin35∘/80=136.5 MW. (b) 138×28/80=48.3 MW. (c) 88.2 to 184.8 MW. (d) sin(35∘+ρ)=(180−136.5)/48.3=0.900, so ρ=29.1∘ (the other root, 80.9∘, gives a more negative Qr). A target of 260 MW is outside the range and is physically infeasible even though a controller would accept the reference.

#### Example 8.32. IPFC: unity power factor at the receiving end of line 1

Two identical lines have V=1 pu, X=0.5 pu and δ=30∘; both IPFC converters can inject 0.25 pu. Converter 1 must hold Q1r=0 while maximizing P1r. Find (a) ρ1; (b) P1r; (c) P1pq and Q1pq; (d) the injection angles of converter 2; (e) the resulting power in line 2.

Solution. (a) cos(δ+ρ1)=−Q0X/(VVpq)=0.536, so ρ1=27.60∘. (b) 1.422 pu. (c) P1pq=0.191 pu and Q1pq=0.300 pu. (d) Converter 2 must absorb 0.191 pu: ρ2=−152.4∘ or 122.4∘. (e) P2r=0.578 pu (Q2r=−0.536 pu) or 1.232 pu (Q2r=−0.711 pu). The second choice raises the flow in both lines; the first transfers power from line 2 to line 1.

#### Example 8.33. IPFC DC-link dynamics

An IPFC DC capacitor has an energy-storage constant Hdc=0.01 s, defined as the stored DC energy at Vdc=1 pu divided by the three-phase power base. Converter 2 supplies 0.25 pu to the DC link while converter 1 absorbs 0.20 pu from it. Find (a) the net power into the link; (b) the exact DC voltage after 10 ms, neglecting losses; (c) the small-signal approximation; (d) the conclusion.

Solution. (a) 0.25−0.20=0.05 pu. (b) Stored energy is proportional to Vdc2, so the normalized energy rises from 1.0 to 1+0.05×0.010/0.010=1.05 and Vdc=1.05=1.0247 pu. (c) Linearizing Wdc=HdcVdc2 about 1 pu gives dΔVdc/dt=ΔP/(2Hdc)=2.5 pu/s, so ΔVdc≈0.025 pu after 10 ms, in close agreement. (d) A 0.05 pu imbalance moves the DC voltage by about 2.5 % in 10 ms, so the DC-voltage controller must act quickly. Using ΔVdc=ΔP Δt/Hdc would overestimate the excursion by a factor of two.

#### Example 8.34. Balancing two parallel lines

Two parallel lines of 0.3 pu and 0.6 pu share 2.3 pu. Find (a) the natural sharing; (b) the series reactance that equalizes the flows; (c) the approximate series voltage needed in line 1.

Solution. (a) 1.533 pu and 0.767 pu. (b) Line 1 must look like 0.6 pu, so 0.3 pu is added. (c) Vq≈0.3×1.15=0.345 pu at the equalized current, a substantial injection at high current.

#### Example 8.35. Generalized IPFC power balance

Four converters share a DC link. Converters 1, 2 and 3 deliver +0.15, −0.08 and −0.04 pu to their lines. Converter 4 injects 0.1 pu into a line carrying 0.9 pu. Find (a) P4pq; (b) the angle between V4pq and I4.

Solution. (a) From Equation (8.9), P4pq=−(0.15−0.08−0.04)=−0.03 pu (converter 4 absorbs). (b) cosϕ=−0.03/(0.1×0.9)=−0.333, so ϕ=109.5∘.

#### Example 8.36. Quadrature booster on a 220 kV line

A quadrature booster injects 20 kV (phase) into a 220 kV line (Vph=127.0 kV) of X=50 Ω at δ=25∘. Find (a) the phase shift; (b) the effective voltage; (c) the power before and after.

Solution. (a) tan−1(20/127)=8.95∘. (b) 1272+202=128.6 kV. (c) P0=3Vph2sin25∘/X=409.1 MW and P=3×128.6×127.0×sin33.95∘/50=547.2 MW. Part of the increase comes from the 1.2 % magnitude rise, which an ideal phase shifter would not produce.

#### Example 8.37. TCPAR on a 132 kV line

A lossless 132 kV line has X=40 Ω and operates at 30∘. Find P and the reactive power supplied at each end for σ=0, +10∘ and −10∘.

Solution. P=V2sin(δ+σ)/X: 217.8, 280.0 and 149.0 MW. With equal end voltages each end supplies V2(1−cos(δ+σ))/X: 58.4, 101.9 and 26.3 Mvar, so the line absorbs twice these values in total.

#### Example 8.38. Ideal phase shifter

An ideal phase shifter injects 0.4 pu. Find (a) σ; (b) the injection angle relative to Vs; (c) the power at δ=30∘ on a 0.3 pu line (V=1 pu) when the shift opposes the angle.

Solution. (a) From Equation (8.13), σ=2sin−1(0.2)=23.07∘. (b) (180∘+23.07∘)/2=101.5∘. (c) P=sin6.93∘/0.3=0.402 pu.

#### Example 8.39. Ternary TCVR

A TCVR has three ternary windings with a smallest step of 5 kV. Find (a) the number of levels; (b) the maximum boost and buck; (c) the winding voltages; (d) the resolution.

Solution. (a) 27. (b) ±13×5=±65 kV. (c) 5, 15 and 45 kV. (d) 5 kV per step.

#### Example 8.40. Thyristor tap-changer harmonics

Taps of 10 kV and 12 kV (peak) feed a resistive load; the upper switch fires at α=60∘ in each half cycle. Find (a) the fundamental amplitude; (b) its phase shift; (c) the 3rd, 5th and 7th harmonics; (d) the THD of these three.

Solution. Fourier analysis of the switched waveform gives (a) 11.62 kV; (b) −2.36∘; (c) 0.477, 0.276 and 0.138 kV; (d) 0.4772+0.2762+0.1382/11.62=4.9 %.

#### Example 8.41. Loop-flow control with a PAR

Two parallel paths of 0.3 pu and 0.6 pu carry 2.3 pu in total. Find the phase shift in the 0.6 pu path that equalizes the flows (a) if the total transfer of 2.3 pu is maintained; (b) if instead the angle across the corridor is held at its original value.

Solution. The original angle is θ=2.3/(1/0.3+1/0.6)=0.46 rad. (a) For 1.15 pu in each path, line 1 needs θ=0.345 rad, so the corridor angle falls to 0.345 rad, and line 2 needs (0.345+σ)/0.6=1.15, giving σ=0.345 rad (19.8∘). (b) With θ=0.46 rad held, σ=0.23 rad (13.2∘) raises line 2 to 1.15 pu while line 1 stays at 1.533 pu, so the total rises to 2.68 pu. The network angle is generally part of the solution, not a fixed input.

#### Example 8.42. VSC-based regulator power exchange

A series VSC injects 5 kV in phase with the bus voltage into a line carrying 500 A at 0.866 power factor lagging. Find, per phase, (a) the real power; (b) the reactive power; (c) the converter rating.

Solution. (a) 5×500cos30∘=2.17 MW. (b) 5×500sin30∘=1.25 Mvar. (c) 2.5 MVA. The real power must be supplied by a shunt converter or a store.

#### Example 8.43. IPC120 powers

An IPC120 with B1=−1 pu and B2=+1 pu connects buses with VS=VR=1 pu at δSR=15∘. Find (a) δB1 and δB2; (b) P; (c) QS and QR.

Solution. (a) 75∘ and −45∘. (b) From Equation (8.16), P=0.966+0.707=1.673 pu, which equals 2×0.866cos15∘ from Equation (8.18). (c) From Equation (8.17), −QS=QR=−(1−cos75∘)+(1−cos45∘)=−0.448 pu. Terminal powers alone do not reveal the internal branch currents.

## Unsolved Practice Problems

Problem 8.1 A UPFC on a line with V=1 pu, X=0.4 pu, δ=45∘ and Vpq,max=0.2 pu must deliver Pr=1.8 pu. Find P0, Q0, the circle radius, the maximum power, and the injection angle (with the corresponding Qr) that gives 1.8 pu with the larger reactive delivery.

Problem 8.2 For V=1 pu, X=0.6 pu and δ=60∘, find the centre and radius of the UPFC control circle for Vpq,max=0.3 pu.

Problem 8.3 A 400 kV line of 100 Ω operates at 40∘ with a UPFC injecting up to 30 kV. Find the power range.

Problem 8.4 Explain, with the DC-balance equation, why an IPFC cannot supply net real power to all its lines simultaneously without a shunt converter or storage.

Problem 8.5 A ternary TCPAR has four windings with a 3 kV smallest step. Find the number of levels and the maximum injection.

Problem 8.6 An injection IPC has ψ1=−20∘, ψ2=+20∘, X=0.5 pu and VS=VR=1 pu. Find P at δSR=10∘ and 25∘.

Problem 8.7 Find the phase shift produced by an ideal phase shifter injecting 0.25 pu.

Problem 8.8 A quadrature booster injects 0.15 pu. Find the phase shift and the magnitude of the effective sending voltage.

Problem 8.9 A 33 kV network has a symmetrical fault current of 12 kA; the breakers are rated 8 kA. Find the reactance a current limiter must add.

Problem 8.10 A series-resonant SSFCL at 11 kV, 50 Hz uses L1=20 mH with a source reactance of 0.5 Ω. Find C1 and the limited symmetrical fault current.

Problem 8.11 A 400 kV arrester clamps at 1.7 pu of the peak phase voltage. Find the clamping voltage, and the TCVL level if 25 % of the stack is bypassed.

Problem 8.12 A 66 kV capacitor bank of 60 μF per phase is energized through 1.5 mH. Find f0, Z0 and the inrush peak for a discharged bank closed at the voltage peak.

Problem 8.13 By what factor does the current of a ZnO block rise when its voltage rises by 10 %, for α=25 and α=40?

Problem 8.14 Compare a UPFC, an IPFC, a TCPAR and an APST for relieving a congested 400 kV corridor with a parallel underused path, a weak voltage at the receiving bus, and a tight budget.

Problem 8.15 A modular series converter must inject 24 kV with cells rated 3.2 kV and must tolerate two bypassed cells. Find the minimum number of cells and the per-cell voltage in normal operation.

Problem 8.16 A converter port with Zc=jωLf+Kpe−jωTd has Td=100 μs. Above what frequency is its real part negative?

Problem 8.17 A series converter emulates 0.10 pu of capacitive reactance on a line of ZL=j0.40 pu protected by a zone 1 set at 85 %. Find the effective zone-1 reach while the converter is active.

## Answer Key (Unsolved Problems)

8.1 1.768 pu; −0.732 pu; 0.5 pu; 2.268 pu; ρ=−41.3∘ with Qr=−0.233 pu (the other root, 131.3∘, gives Qr=−1.231 pu).

8.2 (1.443, −0.833) pu; 0.5 pu.

8.3 P0=1028.5 MW; range 908.5 to 1148.5 MW.

8.4 ∑Pk,pq=0 without a shunt converter or store, so power delivered to some lines must be drawn from others.

8.5 81 levels; ±120 kV.

8.6 1.347 pu; 1.240 pu.

8.7 14.36∘.

8.8 8.53∘; 1.011 pu.

8.9 0.794 Ω.

8.10 506.6 μF; 936 A.

8.11 555.2 kV; 416.4 kV.

8.12 530.5 Hz; 5.0 Ω; 10.8 kA.

8.13 10.8 and 45.3.

8.14 Open-ended. A TCPAR or APST solves the flow sharing at low cost; the weak receiving voltage favours a UPFC (or a TCPAR plus a STATCOM); the APST is the cheapest if the required angle range is predictable.

8.15 10 cells; 2.4 kV per cell.

8.16 2.5 kHz.

8.17 m≤(0.34+0.10)/0.40=1.10, that is, 110 % of the line.

## References

[1] L. Gyugyi, “Unified power-flow control concept for flexible AC transmission systems,” IEE Proceedings C, vol. 139, no. 4, pp. 323-331, 1992.

[2] L. Gyugyi, C. D. Schauder, S. L. Williams, T. R. Rietman, D. R. Torgerson and A. Edris, “The unified power flow controller: a new approach to power transmission control,” IEEE Transactions on Power Delivery, vol. 10, no. 2, pp. 1085-1097, 1995.

[3] N. G. Hingorani and L. Gyugyi, Understanding FACTS: Concepts and Technology of Flexible AC Transmission Systems. New York: IEEE Press, 2000.

[4] K. K. Sen and M. L. Sen, Introduction to FACTS Controllers: Theory, Modeling, and Applications. Hoboken, NJ: Wiley-IEEE Press, 2009.

[5] K. R. Padiyar, FACTS Controllers in Power Transmission and Distribution. New Delhi: New Age International, 2007.

[6] C. Schauder et al., “Operation of the unified power flow controller (UPFC) under practical constraints,” IEEE Transactions on Power Delivery, vol. 13, no. 2, pp. 630-639, 1998.

[7] B. A. Renz, A. Keri, A. S. Mehraban, C. Schauder, E. Stacey, L. Kovalsky, L. Gyugyi and A. Edris, “AEP unified power flow controller performance,” IEEE Transactions on Power Delivery, vol. 14, no. 4, pp. 1374-1381, 1999.

[8] L. Gyugyi, K. K. Sen and C. D. Schauder, “The interline power flow controller concept: a new approach to power flow management in transmission systems,” IEEE Transactions on Power Delivery, vol. 14, no. 3, pp. 1115-1123, 1999.

[9] Y. H. Song and A. T. Johns (Eds.), Flexible AC Transmission Systems (FACTS). London: IEE, 1999.

[10] X.-P. Zhang, C. Rehtanz and B. Pal, Flexible AC Transmission Systems: Modelling and Control. Berlin: Springer, 2006.

[11] B. Fardanesh, M. Henderson, B. Shperling, S. Zelingher, L. Gyugyi, B. Lam, R. Adapa, C. Schauder, J. Mountford and A. Edris, “Convertible static compensator: application to the New York transmission system,” CIGRE Session, Paper 14-103, Paris, 1998.

[12] K. K. Sen and M. L. Sen, “Introducing the family of ‘Sen’ transformers: a set of power flow controlling transformers,” IEEE Transactions on Power Delivery, vol. 18, no. 1, pp. 149-157, 2003.

[13] J. Brochu, Interphase Power Controllers. Montréal: Polytechnic International Press, 1999.

[14] “Operational aspects and benefits of interphase power controllers with conventional or electronically switched phase-shifting devices: a robust FACTS application,” CIGRE Session, Paper 38-101, Paris, 1998.

[15] A. Safaei, M. Zolfaghari, M. Gilvanejad and G. B. Gharehpetian, “A survey on fault current limiters: development and technical aspects,” International Journal of Electrical Power & Energy Systems, vol. 118, Art. no. 105729, 2020, doi: 10.1016/j.ijepes.2019.105729.

[16] IEC 60909-0:2016, Short-circuit currents in three-phase a.c. systems, Part 0: Calculation of currents. Geneva: IEC, 2016.

[17] A. Ghosh and G. Ledwich, Power Quality Enhancement Using Custom Power Devices. Boston: Kluwer, 2002.

[18] IEC 60099-4:2014, Surge arresters, Part 4: Metal-oxide surge arresters without gaps for a.c. systems. Geneva: IEC, 2014.

[19] X. Wang, H. Wang, J. Yang, Z. Xu, W. Sun, C. Wu and C. Li, “Application of 500 kV UPFC in Suzhou southern power grid,” The Journal of Engineering, vol. 2019, no. 16, pp. 2580-2584, 2019, doi: 10.1049/joe.2018.8556.

[20] D. Divan and H. Johal, “Distributed FACTS: a new concept for realizing grid power flow control,” IEEE Transactions on Power Electronics, vol. 22, no. 6, pp. 2253-2260, 2007.

[21] F. Kreikebaum, D. Das, Y. Yang, F. Lambert and D. Divan, “Smart Wires: a distributed, low-cost solution for controlling power flows and monitoring transmission lines,” in Proc. IEEE PES Innovative Smart Grid Technologies Conference Europe, Gothenburg, 2010.

[22] S. Yang, Y. Liu, X. Wang, D. Gunasekaran, U. Karki and F. Z. Peng, “Modulation and control of transformerless UPFC,” IEEE Transactions on Power Electronics, vol. 31, no. 2, pp. 1050-1063, 2016.

[23] A. Mandal, K. M. Muttaqi, M. R. Islam and D. Sutanto, “A novel architecture of the solid-state unified power flow controller and its integration into the power grid,” Electric Power Systems Research, vol. 241, Art. no. 111296, 2025, doi: 10.1016/j.epsr.2024.111296.

[24] D. Keshavarzi, A. Koehler, W. H. Wellssow and S. M. Goetz, “Entirely transformerless universal direct-injection power-flow controller,” arXiv:2511.14209, 2025.

[25] B. H. Alajrash, M. Salem, M. Swadi, T. Senjyu, M. Kamarol and S. Motahhir, “A comprehensive review of FACTS devices in modern power systems: addressing power quality, optimal placement, and stability with renewable energy penetration,” Energy Reports, vol. 11, pp. 5350-5371, 2024, doi: 10.1016/j.egyr.2024.05.011.

[26] D. K. Molzahn and I. A. Hiskens, “A survey of relaxations and approximations of the power flow equations,” Foundations and Trends in Electric Energy Systems, vol. 4, no. 1-2, pp. 1-221, 2019.

[27] X. Wang and F. Blaabjerg, “Harmonic stability in power electronic-based power systems: concept, modeling, and analysis,” IEEE Transactions on Smart Grid, vol. 10, no. 3, pp. 2858-2870, 2019.

[28] J. Sun, “Impedance-based stability criterion for grid-connected inverters,” IEEE Transactions on Power Electronics, vol. 26, no. 11, pp. 3075-3078, 2011.

[29] B. Fan, T. Liu, F. Zhao, H. Wu and X. Wang, “A review of current-limiting control of grid-forming inverters under symmetrical disturbances,” IEEE Open Journal of Power Electronics, vol. 3, pp. 955-969, 2022.

[30] J. Häfner and B. Jacobson, “Proactive hybrid HVDC breakers: a key innovation for reliable HVDC grids,” in Proc. CIGRE Symposium, Bologna, 2011.